## 目录 (hidden)
T3 50HZ R22 Ca
商用空调单元机专业数据目录
T3 50HZ R22 CF
T3 50HZ R22 LD
T3 50HZ R22 MD
维护记录表
T3 60Hz R22 Ca
T3 60Hz R22 CF
T3 60Hz R22 LD
T3 60Hz R22 MD
T3 50Hz R22 Universal Outdoor Units
T3 60Hz R22 Universal Outdoor Units
T3 60Hz R22 HD

## Outdoor Units SAU-U1-A_on off
Model |  |  | SAU12U1-A | SAU18U1-A | SAU24U1-A | SAU36U1-A | SAU48U1-A | SAU60U1-A
Code |  |  | 16107022000017 | 16107022000019 | 16107022000018 | 16107022000020 | 16107022000022 | 16107022000023
Power Supply |  | V~,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 380~415,50,3 | 380~415,50,3 | 380~415,50,3
Capacity | Cooling | Btu/h | 12000 | 18000 | 24000 | 36000 | 48000 | 60000
|  | TR | 1 | 1.5 | 2 | 3 | 4 | 5
|  | kW | 3.6 | 5.3 | 7.2 | 10.6 | 14 | 17.6
| Heating | Btu/h | 13306.8 | 19789.6 | 27568.96 | 39920.4 | 52886 | 63122
|  | TR | 1.1089 | 1.6491 | 2.2974 | 3.3267 | 4.4072 | 5.2602
|  | kW | 3.9 | 5.8 | 8.08 | 11.7 | 15.5 | 18.5
Max. Input Consumption |  | W | 1750 | 2520 | 3200 | 5100 | 5950 | 7800
Max. Current |  | A | 7.764 | 12.1 | 17.8 | 9.5 | 13.5 | 16.5
Compressor | Model |  | ASL150UV-C7LU | ASL201UV-C7EQ | ASH286UV-C8DU | ATH420UC-C9EU | ATE498SC3Q9RK1 | ATE590SC3Q9JK
| Type |  | Rotary | Rotary | Rotary | Twin Rotary | Twin Rotary | Twin Rotary
| Brand |  | HIGHLY | HIGHLY | HIGHLY | HIGHLY | HIGHLY | HIGHLY
| Capacity | W | 3555 | 4900 | 6980 | 10150 | 12650 | 14850
| Input | W | 1200 | 1633 | 2320 | 3350 | 4130 | 4950
| Rated Current(RLA) | A | 5.55 | 7.65 | 10.9 | 6.9 | 7.2 | 8.7
| Locked Rotor Amp(LRA) | A | 30 | 38 | 60 | 66 | 69 | 65
| Thermal Protection temp. | ℃ | 150 | 150 | 160 | 180 | 160 | 180
| Capacitor | uF | 35 | 50 | 70 | / | / | /
| Refrigerant Oil | ml | 450 | 480 | 570 | 840 | 1600 | 1850
Outdoor fan motor | Model |  | YDK31-6F | YDK31-6F | YDK68-6A | YDK150-6C-420 | YDK60-6H | YDK60-6H
| Brand |  | Tongdeli | Tongdeli | Sinjun | Weiling | Sinjun/Welling | Sinjun/Welling
| Output Power x Fan quantity | W | 31×1 | 31×1 | 68×1 | 150×1 | 60×2 | 60×2
| Capacitor | μF | 2.5 | 2.5 | 4 | 6 | 3.5×2 | 3.5×2
| Speed | r/min | 900 | 900 | 880 | 820 | 750 | 750
Coil | a.Number Of Row |  | 1 | 2 | 2 | 2 | 1.5 | 1.5
| b.Tube Pitch(a)x Row Pitch(b) | mm | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05 | 22×19.05
| c.Fin Pitch | mm | 1.4 | 1.4 | 1.5 | 1.4 | 1.4 | 1.4
| d.Fin Material |  | Hydrophilic aluminum wide fin | Hydrophilic aluminum wide fin | Hydrophilic aluminum wide fin | Hydrophilic aluminum wide fin | Hydrophilic aluminum wide fin | Hydrophilic aluminum wide fin
| e.Tube Outside Dia.And Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
| f.Coil Length x Height x Width | mm | 853×506×19.05 | 853×506×38.1 | 763×616×38.1 | 894×814×38.1 | 973×1320×38.1 | 973×1320×38.1
| g.Heat Exchanging Area | ㎡ | 10.4663 | 15.9877 | 22.1 | 35.2973 | 47.6185 | 47.6185
Air Flow Volume |  | CFM | 1470.5882 | 1470.5882 | 1617.6471 | 1876.4706 | 3764.7059 | 3764.7059
|  | m3/h | 2500 | 2500 | 2750 | 3190 | 6400 | 6400
Noise Level |  | dB(A) | 53 | 55 | 56 | 62 | 60 | 60
Dimension(W×D×H) | Net | mm | 800×286×530 | 800×286×530 | 822×302×655 | 903×354×857 | 940×368×1366 | 940×368×1366
| Packing | mm | 920×400×620 | 920×400×620 | 945×430×725 | 1030×410×980 | 1080×460×1500 | 1080×460×1500
Weight | Net | kg | 34 | 38 | 50 | 71 | 101 | 102
| Gross | kg | 37 | 41 | 54 | 81 | 112 | 113
Refrigerant type/Quantity | Type |  | R410A | R410A | R410A | R410A | R410A | R410A
| Charged Volume | g | 800 | 1250 | 1400 | 2150 | 2750 | 2900
Design Pressure |  | MPa | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
Refrigerant Pipe | Liquid Side | mm | 6.35 | 6.35 | 9.52 | 9.52 | 9.52 | 9.52
| Gas Side | mm | 12.7 | 12.7 | 15.88 | 15.88 | 19.05 | 19.05
| Max. Length | m | 15 | 20 | 30 | 50 | 50 | 50
| Max. Height | m | 10 | 15 | 15 | 30 | 30 | 30
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temp (Cooling/Heating) |  | ℃ | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24
Connection Wiring | Power Wiring（Indoor） | mm2 | 3×2.5mm2 | 3×2.5mm2 | / | 3×4mm2 | 3×4mm2 | 3×4mm2
| Power Wiring（Outdoor） | mm2 | / | / | 3×4mm2 | 5×4mm2 | 5×4mm2 | 5×4mm2
| Signal Wiring | mm2 | 3×2.5mm2+2×1mm2 | 3×2.5mm2+2×1mm2 | 3×1mm2+3×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Stuffing Quantity | 20/40/40H | Unit | 123/255/340 | 102/204/272 | 102/204/204 | 60/124/124 | 26/54/54 | 26/54/54
Remark:The above designs and specifications are subject to change of product improvement without prior notice.
| Rated Cooling Power Input | kW | 1.14 | 1.65 | 2.12 | 3.55 | 4.66 | 5.49
| Rated Heating Power Input | kW | 1.15 | 1.7 | 2.15 | 3.3 | 4.92 | 5.76
| Rated Cooling Current | A | 5.41 | 7.95 | 10.35 | 6.01 | 9.02 | 10.52
| Rated Heating Current | A | 1.14 | 1.65 | 2.12 | 3.55 | 4.66 | 5.49
| Annual electricity consumption |  | 570 | 825 | 1060 | 1775 | 2330 | 2745
| EER |  | 3.1579 | 3.2121 | 3.3962 | 2.9859 | 3.0043 | 3.2058
| COP |  | 3.3913 | 3.4118 | 3.7581 | 3.5455 | 3.1504 | 3.2118
| Class of energy efficiency (cooling) |  | B | A | A | C | C | A
| Class of efficiency (heating) |  | C | B | A | B | D | C
| Class of moisture protection |  | IPX4 | IPX4 | IPX4 | IPX4 | IPX4 | IPX4
| Electrical protection class |  | Class I | Class I | Class I | Class I | Class I | Class I

## 60Hz Outdoor Units (hidden)
Return
Model |  |  | ALT-C18/2(U) | ALT-H18/2(U) | ALT-C24/2(U) | ALT-H24/2(U) | ALT-C36/2(U) | ALT-H36/2(U) | ALT-C48/2(U) | ALT-H48/2(U) | AL-C60/2(U) | AL-H60/2(U) | ALT-C48/6(U) | ALT-H48/6(U) | ALT-C60/6(U) | ALT-H60/6(U)
Factory Model |  |  | ALT-18A2(T) | ALT-H18A2(T) | ALT-24A2(T) | ALT-H24A2(T) | ALT-36A2(T) | ALT-H36A2(T) | ALT-48A2(T) | ALT-H48A2(T) | ALT-60A2(T) | ALT-H60A2(T) | ALT-48A6(T) | ALT-H48A6(T) | ALT-60B6(T) | ALT-H60B6(T)
Code |  |  | 65965303520 | 65965303160 | 65970100535 | 65965303470 | 65970100577 | 65970101328 | 65964904270 | 65965303200 | / | 65965303210 | 65970100621 | / | 65965303530 | 65970101326
Power Supply |  | V~,Hz,Ph | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 380,60,3 | 380,60,3 | 380,60,3 | 380,60,3
Max. Input Consumption |  | kW | 2.84 | 2.84 | 3.91 | 3.91 | 5.9 | 5.9 | 7.3 | 7.3 | 8.1 | 8.1 | 7.2 | 7.2 | 7.8 | 7.8
Max. Current |  | A | 14.36 | 14.36 | 20.1 | 20.1 | 26.9 | 26.9 | 33.2 | 33.2 | 36.9 | 36.9 | 13.25 | 13.25 | 14.16 | 14.16
Capacity | Cooling | Btu/h | 18000 | 18000 | 24000 | 24000 | 36000 | 36000 | 48000 | 48000 | 55000 | 55000 | 48000 | 48000 | 55000 | 55000
|  | TR | 1.5 | 1.5 | 2.0387 | 2.0387 | 3 | 3 | 3.9942 | 3.9942 | 4.6 | 4.6 | 3.9942 | 3.9942 | 4.6 | 4.6
|  | kW | 5.2 | 5.2 | 7.1 | 7.1 | 10.5 | 10.5 | 14.064 | 14.064 | 16 | 16 | 14.064 | 14.064 | 16 | 16
| Heating | Btu/h | / | 19000 | / | 27000 | / | 37500 | / | 50000 | / | 60000 | / | 50000 | / | 60000
|  | TR | / | 1.5893 | / | 2.2596 | / | 3.1383 | / | 4.1845 | / | 5.1 | / | 4.1845 | / | 5.1
|  | kW | / | 5.5653 | / | 7.9086 | / | 10.9842 | / | 14.6456 | / | 17.5 | / | 14.6456 | / | 17.5
Compressor | Model |  | SHZ83LC4-E | SHZ83LC4-E | SHW73TC4-E | SHW73TC4-E | C-SBR120H16P | C-SBR120H16P | C-SBR145H16P | C-SBR145H16P | C-SBR165H16P | C-SBR165H16P | C-SB303H9A | C-SB303H9A | C-SB353H9A | C-SB353H9A
| Type |  | ROTARY | ROTARY | ROTARY | ROTARY | SCROLL | SCROLL | SCROLL | SCROLL | SCROLL | SCROLL | SCROLL | SCROLL | SCROLL | SCROLL
| Brand |  | HITACHI | HITACHI | HITACHI | HITACHI | SANYO | SANYO | SANYO | SANYO | SANYO | SANYO | SANYO | SANYO | SANYO | SANYO
| Capacity | W | 6030 | 6030 | 7330 | 7330 | 11900 | 11900 | 14200 | 14200 | 16700 | 16700 | 14200 | 14200 | 16600 | 16600
| Input | W | 2025 | 2025 | 2445 | 2445 | 3900 | 3900 | 4550 | 4550 | 5300 | 5300 | 4400 | 4400 | 5107 | 5107
| Rated Current(RLA) | A | 9.4 | 9.4 | 12 | 12 | 18.6 | 18.6 | 22.6 | 22.6 | 27.1 | 27.1 | 7.5 | 7.5 | 8.74 | 8.74
| Locked Rotor Amp(LRA) | A | 42 | 42 | 65 | 65 | 158 | 158 | 164 | 164 | 154 | 154 | 58 | 58 | 63 | 63
| Thermal Protector Position |  | 125 | 125 | 125 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 145 | 145 | 145 | 145
| Capacitor | uF | 50 | 50 | 60 | 60 | 60 | 60 | 70 | 70 | 80 | 80 | / | / | / | /
| Refrigerant Oil | ml | 600 | 600 | 600 | 600 | 1700 | 1700 | 1400 | 1400 | 1400 | 1400 | 1700 | 1700 | 1700 | 1700
Outdoor fan motor | Model |  | YDK65-6C-60 | YDK65-6C-60 | YDK68-6B-60 | YDK68-6B-60 | YDK150-6D-60-T3 | YDK150-6D-60-T3 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3
| Brand |  | AUX | AUX | AUX | AUX | WEITELI | WEITELI | AUX | AUX | AUX | AUX | AUX | AUX | AUX | AUX
| Output Power | W | 65 | 65 | 68 | 68 | 150 | 150 | 70×2 | 70×2 | 70×2 | 70×2 | 70×2 | 70×2 | 70×2 | 70×2
| Capacitor | uF | 5 | 5 | 4 | 4 | 6 | 6 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Speed | r/min | 860 | 860 | 830 | 830 | 860 | 860 | 880 | 880 | 880 | 880 | 880 | 880 | 880 | 880
Coil | a.Number Of Row |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 3 | 3
| b.Tube Pitch(a)x Row Pitch(b) | mm | 22×19.05 | 22×19.05 | 25.4×22 | 25.4×22 | 25.4×22 | 25.4×22 | 25.4×22 | 25.4×22 | 25.4×22 | 25.4×22 | 25.4×22 | 25.4×22 | 25.4×22 | 25.4×22
| c.Fin Spacing | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.4 | 1.4 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| d.Fin Material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| e.Tube Outside Dia.And Material | mm | φ7.94， Inner grooved | φ7.94， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved
| f.Coil Length x Height x Width | mm | 760×484×38.1 | 760×484×38.1 | 733×660.4×44 | 733×660.4×44 | 890×812.8×44 | 890×812.8×44 | 750×1219.2×44 | 750×1219.2×44 | 750×1219.2×66 | 750×1219.2×66 | 750×1219.2×44 | 750×1219.2×44 | 750×1219.2×66 | 750×1219.2×66
| g.Number Of U-Tube |  | 22 | 22 | 26 | 26 | 32 | 32 | 48 | 48 | 72 | 72 | 48 | 48 | 72 | 72
| h. Number Of Circuits |  | 4 | 4 | 4 | 4 | 8 | 8 | 8 | 8 | 6 | 6 | 8 | 8 | 6 | 6
| i.Heat Exchanging Area | ㎡ | 17.66 | 17.66 | 31.83 | 31.83 | 40.7 | 40.7 | 45.3 | 45.3 | 67.9 | 67.9 | 45.3 | 45.3 | 67.9 | 67.9
Air Flow Volume |  | m3/h | 2600 | 2600 | 2790 | 2790 | 3190 | 3190 | 5200 | 5200 | 5200 | 5200 | 5200 | 5200 | 5200 | 5200
Noise Level |  | dB(A) | 55 | 55 | 60 | 60 | 60 | 60 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62
Dimension(W×D×H) | Net | mm | 800x300x590 | 800x300x590 | 800x300x690 | 800x300x690 | 903x354x857 | 903x354x857 | 945x340x1255 | 945x340x1255 | 945x340x1255 | 945x340x1255 | 945x340x1255 | 945x340x1255 | 945x340x1255 | 945x340x1255
| Packing | mm | 930x410x660 | 930x410x660 | 930x410x760 | 930x410x760 | 1030x410x980 | 1030x410x980 | 1090x430x1370 | 1090x430x1370 | 1090x430x1370 | 1090x430x1370 | 1090x430x1370 | 1090x430x1370 | 1090x430x1370 | 1090x430x1370
Weight | Net | kg | 44 | 45 | 55 | 56 | 86 | 88 | 97 | 105 | 110 | 118 | 97 | 105 | 110 | 118
| Gross | kg | 48 | 49 | 59 | 60 | 94 | 96 | 112 | 119 | 117 | 125 | 112 | 119 | 117 | 125
Refrigerant Type | Type |  | R22 | R22 | R22 | R22 | R22 | R22 | R22 | R22 | R22 | R22 | R22 | R22 | R22 | R22
| Charged Volume | kg | 1.2 | 1.3 | 1.8 | 1.97 | 2.2 | 2.2 | 2.85 | 2.85 | 3.8 | 3.8 | 3.1 | 3.1 | 3.89 | 3.89
Design Pressure |  | MPa | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
Refrigerant Pipe | Liquid Side | mm | 6.35 | 6.35 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
| Gas Side | mm | 12.7 | 12.7 | 15.88 | 15.88 | 15.88 | 15.88 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05
| Max. Length | m | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
| Max. Height | m | 15 | 15 | 15 | 15 | 25 | 25 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temp (Cooling/Heating) |  | ℃ | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24
Stuffing Quantity | 20/40/40H | Unit | 102/204/204 | 102/204/204 | 102/204/204 | 102/204/204 | 60/124/124 | 60/124/124 | 43/86/103 | 43/86/103 | 43/86/103 | 43/86/103 | 43/86/103 | 43/86/103 | 43/86/103 | 43/86/103
Remark:The above designs and specifications are subject to change of product improvement without prior notice.

## Cassette type_SAC-C1-A
Model | Indoor |  | SAC12C1-A | SAC18C1-A | SAC24C1-A | SAC36C1-A | SAC48C1-A | SAC60C1-A
| Outdoor |  | SAU12U1-A | SAU18U1-A | SAU24U1-A | SAU36U1-A | SAU48U1-A | SAU60U1-A
| Panel |  | SCP13A1 | SCP13A1 | SCP12A1 | SCP12A1 | SCP12A1 | SCP12A1
Code | Indoor |  | 16106022000055 | 16106022000054 | 16106022000053 | 16106022000056 | 16106022000057 | 16106022000058
| Outdoor |  | 16107022000017 | 16107022000019 | 16107022000018 | 16107022000020 | 16107022000022 | 16107022000023
Power Supply |  | V~,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 220~240,50,1
Capacity | Cooling | Btu/h | 12000 | 18000 | 24000 | 36000 | 48000 | 60000
|  | TR | 1 | 1.5 | 2 | 3 | 4 | 5
|  | kW | 3.6 | 5.3 | 7.2 | 10.6 | 14 | 17.6
| Heating | Btu/h | 13306.8 | 19789.6 | 27568.96 | 39920.4 | 52886 | 63122
|  | TR | 1.1089 | 1.6491 | 2.2974 | 3.3267 | 4.4072 | 5.2602
|  | kW | 3.9 | 5.8 | 8.08 | 11.7 | 15.5 | 18.5
Electric Data | Rated Cooling Power Input | kW | 1.19 | 1.76 | 2.39 | 3.77 | 4.87 | 5.71
| Rated Heating Power Input | kW | 1.2 | 1.8 | 2.5 | 3.5 | 5.13 | 6
| Rated Cooling Current | A | 5.49 | 8.08 | 11.06 | 6.76 | 8.88 | 10.42
| Rated Heating Current | A | 5.63 | 8.27 | 11.59 | 6.28 | 9.33 | 10.88
Performance | EER | W/W | 3.0252 | 3.0114 | 3.0126 | 2.8117 | 2.8747 | 3.0823
|  | (Btu/h)/W | 10.084 | 10.2273 | 10.0418 | 9.5491 | 9.8563 | 10.5079
| COP | W/W | 3.25 | 3.2222 | 3.232 | 3.3429 | 3.0214 | 3.0833
|  | (Btu/h)/W | 11.089 | 10.9942 | 11.0276 | 11.4058 | 10.3092 | 10.5203
Indoor Fan Motor | Model |  | YDK25-6E1 | YDK30-6E1 | XD30A | YDK45-6Q | XD80A | XD80A
| Brand |  | WELLING/Sinjun | WELLING/Sinjun | WELLING/Sinjun | WELLING/Sinjun | WELLING/Sinjun | WELLING/Sinjun
| Output Power x Fan quantity | W | 25*1 | 30*1 | 30*1 | 45*1 | 80*1 | 80*1
| Capacitor | μF | 1.5 | 2.5 | 2.5 | 3 | 3 | 4
| Speed (Hi/Mi/Lo) | r/min | 850/750/650 | 920/850/750 | 500/430/320 | 650/520/450 | 695/585/495 | 695/585/495
Indoor Coil | a.Number Of Row |  | 2 | 2 | 2 | 2 | 2 | 3
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
| c.Fin Pitch | mm | 1.5 | 1.5 | 1.4 | 1.4 | 1.4 | 1.4
| d.Fin Material |  | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin
| e.Tube Outside Dia.And Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
| f.Coil Length x Height x Width | mm | 1160×184.5×25.4 | 1160×184.5×25.4 | 2142×205×25.4 | 2142×205×25.4 | 2142×246×25.4 | 2142×246×25.4
| g.Heat Exchanging Area | m2 | 4.32 | 5.76 | 11.34 | 12.7597 | 15.5952 | 15.5952
Indoor Unit | Indoor Air Flow (Hi/Mi/Lo) | m3/h | 620/496/434 | 900/720/630 | 1300/1040/910 | 1500/1200/1050 | 1800/1440/1260 | 1800/1440/1260
| Noise Level(Hi/Mi/Lo) | dB(A) | 41/38/32 | 41/38/32 | 45/42/36 | 48/45/39 | 50/47/41 | 50/47/41
| Extemal Static Pressure | Pa | 0 | 0 | 0 | 0 | 0 | 0
Dimension(W×D×H) | Net(Body) | mm | 615×615×263 | 615×615×263 | 835×835×250 | 835×835×250 | 835×835×290 | 835×835×290
| Packing(Body) | mm | 700×700×330 | 700×700×330 | 910×910×310 | 910×910×310 | 910×910×350 | 910×910×350
| Net(Panel) | mm | 650×650×55 | 650×650×55 | 950×950×55 | 950×950×55 | 950×950×55 | 950×950×55
| Packing(Panel) | mm | 710×710×80 | 710×710×80 | 1000x1000x100 | 1000x1000x100 | 1000x1000x100 | 1000x1000x100
Weight | Net(Body) | kg | 17.5 | 18 | 24 | 24 | 26.5 | 26.5
| Gross(Body) | kg | 21.5 | 22 | 27.5 | 27.5 | 30.5 | 30.5
| Net(Panel) | kg | 3 | 3 | 5 | 5 | 5 | 5
| Gross(Panel) | kg | 5 | 5 | 7 | 7 | 7 | 7
Refrigerant Pipe | Liquid Side | mm | 6.35 | 6.35 | 9.52 | 9.52 | 9.52 | 9.52
| Gas Side | mm | 12.7 | 12.7 | 15.88 | 15.88 | 19.05 | 19.05
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | -5~49/-15~24 | -5~49/-15~24 | -5~49/-15~24 | -5~49/-15~24 | -5~49/-15~24 | -5~49/-15~24
Application Area |  | m2 | 13-21 | 21-35 | 28-47 | 42-70 | 56-93 | 64-107
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×2.5mm2 | 3×4mm2 | / | 3×4mm2 | 3×4mm2 | 3×4mm2
| Power Wiring( Outdoor) | mm2 | / | / | 3×6mm2 | 5×4mm2 | 5×4mm2 | 5×4mm2
| Signal Wiring | mm2 | 3×1.5mm2+2×1mm2 | 3×2.5mm2+2×1mm2 | 3×2.5mm2+3×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Wired Controller |  |  | YKR-K/001E | YKR-K/001E | YKR-K/001E | YKR-K/001E | YKR-K/001E | YKR-K/001E
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 72/146/162 | 57/120/144 | 39/76/96 | 30/70/76 | 26/54/54 | 26/54/54
Remark:The above designs and specifications are subject to change of product improvement without prior notice.
| Annual electricity consumption |  | 595 | 880 | 1195 | 1885 | 2435 | 2855
| Class of energy efficiency (cooling) |  | B | B | B | C | C | B
| Class of energy efficiency (heating) |  | C | C | C | C | D | D
| Class of moisture protection |  | IPX4 | IPX4 | IPX4 | IPX4 | IPX4 | IPX4
| Electrical protection class |  | Class I | Class I | Class I | Class I | Class I | Class I

## Ceiling&Floor_SACF-D1-A
Model | Indoor |  | SACF18D1-A | SACF24D1-A | SACF36D1-A | SACF48D1-A | SACF60D1-A
| Outdoor |  | SAU18U1-A | SAU24U1-A | SAU36U1-A | SAU48U1-A | SAU60U1-A
Code | Indoor |  | 16109022000011 | 16109022000007 | 16109022000008 | 16109022000009 | 16109022000010
| Outdoor |  | 16107022000019 | 16107022000018 | 16107022000020 | 16107022000022 | 16107022000023
Power Supply |  | V~,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 220~240,50,1
Capacity | Cooling | Btu/h | 18000 | 24000 | 36000 | 48000 | 60000
|  | kW | 5.3 | 7.2 | 10.6 | 14 | 17.6
| Heating | Btu/h | 20000 | 27500 | 40000 | 53000 | 63500
|  | kW | 5.8 | 8.08 | 11.7 | 15.5 | 18.5
Electric Data | Rated Cooling Power Input | kW | 1.7208 | 2.18 | 3.7722 | 4.87 | 5.7091
| Rated Heating Power Input | kW | 1.77 | 2.5 | 3.5 | 5.13 | 5.97
| Rated Cooling Current | A | 7.9 | 10.09 | 6.76 | 8.88 | 10.42
| Rated Heating Current | A | 8.13 | 11.59 | 6.28 | 9.33 | 10.83
Performance | EER | W/W | 3.08 | 3.31 | 2.81 | 2.8747 | 3.08
| COP | W/W | 3.28 | 3.24 | 3.3429 | 3.02 | 3.1
Indoor Fan Fotor | Model |  | YSK-40W-4 | YSK-70W-4 | YSK-70W-4 | YSK-105W-4 | YSK-105W-4
| Brand |  | Weiling | Weiling | Weiling | Weiling | Weiling
| Output Power x Fan quantity | W | 40x1 | 70x1 | 70x1 | 105 | 105
| Capacitor | uF | 2.5 | 4 | 4 | 5 | 4
| Speed (Hi/Mi/Lo) | r/min | 1250/1100/900 | 1386/1108/970 | 1386/1108/970 | 1387/1108/970 | 1387/1108/970
Indoor Coil | a.Number Of Row |  | 3 | 3 | 3 | 3 | 3
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 22×19.05 | 20.5×12.7 | 22×19.05
| c.Fin Spacing | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| d.Fin Material |  | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin
| e.Tube Outside Dia.and Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7.94， Inner grooved | φ7， Inner grooved | φ7.94， Inner grooved
| f.Coil Length x Height x Width | mm | 599×246×38.1 | 950×246×38.1 | 950×242×57.15 | 1300×246×38.1 | 1300×242×57.15
| g.Heat Exchanging Area | m2 | 6.3 | 10 | 15.02 | 13.69 | 20.55
Indoor Unit | Indoor Air Flow (Hi/Mi/Lo) | m3/h | 850/680/595 | 1200/960/840 | 1500/1200/1050 | 1800/1440/1260 | 1800/1440/1260
| Noise Level(Hi/Mi/Lo) | dB(A) | 43/40/34 | 46/43/38 | 50/47/41 | 51/48/42 | 51/48/42
| External Static Pressure | Pa | 0 | 0 | 0 | 0 | 0
| Net Dimension (W*H*D) | mm | 930×660×205 | 1280×660×205 | 1280×660×205 | 1631×660×205 | 1631×660×205
| Packing Dimension (W*H*D) | mm | 1010×720×290 | 1360×720×290 | 1360×720×290 | 1710×720×290 | 1710×720×290
| Net Weight | Kg | 25 | 32 | 33 | 44 | 44
| Gross Weight | Kg | 28 | 37 | 40 | 52 | 52
Refrigerant Pipe | Liquid Side | mm | 6.35 | 9.52 | 9.52 | 9.52 | 9.52
| Gas Side | mm | 12.7 | 15.88 | 15.88 | 19.05 | 19.05
| Max. Refrigerant Pipe Length | m | 20 | 30 | 50 | 50 | 50
| Max. Difference In Level | m | 15 | 15 | 30 | 30 | 30
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24
Application Area |  | m2 | 21-35 | 28-47 | 42-70 | 56-93 | 64-107
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×4mm2 | / | 3×4mm3 | 3×4mm3 | 3×4mm3
| Power Wiring( Outdoor) | mm2 | / | 3×6mm2 | 5×4mm3 | 5×4mm3 | 5×4mm3
| Signal Wiring | mm2 | 3×2.5mm2+2×1mm2 | 3×2.5mm2+3×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Wireless Remote Controller |  |  | YKR-K/001E | YKR-K/001E | YKR-K/001E | YKR-K/001E | YKR-K/001E
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 54/115/142 | 50/100/124 | 36/71/88 | 25/54/54 | 25/54/54
Remark:The above designs and specifications are subject to change of product improvement without prior notice.
| Annual electricity consumption |  | 885 | 1250 | 1750 | 2565 | 2985
| Class of energy efficiency (cooling) |  | B | A | C | C | B
| Class of energy efficiency (heating) |  | C | C | C | D | D
| Class of moisture protection |  | IPX4 | IPX4 | IPX4 | IPX4 | IPX4
| Electrical protection class |  | Class I | Class I | Class I | Class I | Class I

## Mid Duct_SAD-D1-A
Model | Indoor |  | SAD18D1-A | SAD24D1-A | SAD36D1-A | SAD48D1-A | SAD60D1-A
| Outdoor |  | SAU18U1-A | SAU24U1-A | SAU36U1-A | SAU48U1-A | SAU60U1-A
Code | Indoor |  | 16113022000047 | 16113022000043 | 16113022000044 | 16113022000045 | 16113022000046
| Outdoor |  | 16107022000019 | 16107022000018 | 16107022000020 | 16107022000022 | 16107022000023
Power Supply |  | V~,Hz,Ph | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 220~240,50,1 | 220~240,50,1
Capacity | Cooling | Btu/h | 18000 | 24000 | 36000 | 48000 | 60000
|  | kW | 5.3 | 7.2 | 10.6 | 14 | 17.6
| Heating | Btu/h | 20000 | 27500 | 40000 | 53000 | 63500
|  | kW | 5.8 | 8.08 | 11.7 | 15.5 | 18.5
Electric Data | Rated Cooling Power Input | kW | 1.732 | 2.236 | 3.7324 | 4.87 | 5.7091
| Rated Heating Power Input | kW | 1.79 | 2.3478 | 3.5 | 5.13 | 6
| Rated Cooling Current | A | 7.95 | 10.37 | 6.69 | 8.88 | 10.42
| Rated Heating Current | A | 8.22 | 10.89 | 6.28 | 9.33 | 10.88
Performance | EER | W/W | 3.06 | 3.21 | 2.84 | 2.87 | 3.08
| COP | W/W | 3.24 | 3.45 | 3.34 | 3.0214 | 3.08
Indoor Fan Fotor | Model |  | YSK100-4 | YSK160-4 | YSK180-4 | YSK180-4 | YSK180-4
| Brand |  | Weiling | Sanxiang/Kangbao | Kangbao | Kangbao | Kangbao
| Output Power x Fan quantity | W | 100 | 160 | 180 | 180 | 180
| Capacitor | uF | 4 | 2.5 | 6 | 6 | 6
| Speed (Hi/Mi/Lo) | r/min | 960/860/840 | 1050/1000/910 | 1200/1120/1060 | 1200/1120/1060 | 1200/1120/1060
Indoor Coil | a.Number Of Row |  | 2 | 3 | 3 | 3 | 3
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
| c.Fin Spacing | mm | 1.5 | 1.6 | 1.6 | 1.6 | 1.6
| d.Fin Material |  | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin
| e.Tube Outside Dia.and Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
| f.Coil Length x Height x Width | mm | 625×369×25.4 | 625×369×38.1 | 625×369×38.1 | 985×369×38.1 | 985×369×38.1
| g.Heat Exchanging Area | m2 | 6.98 | 9.87 | 9.87 | 15.56 | 15.56
Indoor Unit | Indoor Air Flow (Hi/Mi/Lo) | m3/h | 1000/800/700 | 1400/1120/980 | 2000/1600/1400 | 2400/2000/1600 | 2800/2240/1960
| Noise Level(Hi/Mi/Lo) | dB(A) | 44/41/35 | 47/44/38 | 50/47/41 | 53/50/44 | 53/50/44
| External Static Pressure | Pa | 50/80 | 50/80 | 50/80 | 50/80 | 50/80
| Net Dimension (W*H*D) | mm | 890×785×290 | 890×785×290 | 890×785×290 | 1250×785×290 | 1250×785×290
| Packing Dimension (W*H*D) | mm | 1100×870×360 | 1100×870×360 | 1100×870×360 | 1460×870×360 | 1460×870×360
| Net Weight | Kg | 34 | 36 | 36 | 52 | 52
| Gross Weight | Kg | 40 | 42 | 42 | 59 | 59
Refrigerant Pipe | Liquid Side | mm | 6.35 | 9.52 | 9.52 | 9.52 | 9.52
| Gas Side | mm | 12.7 | 15.88 | 15.88 | 19.05 | 19.05
| Max. Refrigerant Pipe Length | m | 20 | 30 | 50 | 50 | 50
| Max. Difference In Level | m | 15 | 15 | 30 | 30 | 30
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | -5~49/-15~24 | -5~49/-15~24 | -5~49/-15~24 | -5~49/-15~24 | -5~49/-15~24
Application Area |  | m2 | 21-35 | 28-47 | 42-70 | 56-93 | 64-107
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×4mm2 | / | 3×4mm3 | 3×4mm3 | 3×4mm3
| Power Wiring( Outdoor) | mm2 | / | 3×6mm2 | 5×4mm3 | 5×4mm3 | 5×4mm3
| Signal Wiring | mm2 | 3×2.5mm2+2×1mm2 | 3×2.5mm2+3×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Wireless Remote Controller |  |  | XK-02 | XK-02 | XK-02 | XK-02 | XK-02
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 42/90/111 | 42/90/108 | 36/72/84 | 25/50/54 | 25/50/54
Remark:The above designs and specifications are subject to change of product improvement without prior notice.
| Annual electricity consumption |  | 866.0131 | 1118.0124 | 1866.1972 | 2435 | 2854.5455
| Class of energy efficiency (cooling) |  | B | A | С | C | B
| Class of energy efficiency (heating) |  | C | B | С | D | D
| Class of moisture protection |  | IPX4 | IPX4 | IPX4 | IPX4 | IPX4
| Electrical protection class |  | Class I | Class I | Class I | Class I | Class I

## T3 60Hz MD (hidden)
Return |  | Model | ALTMD-C18/2 | ALTMD-H18/2 | ALTMD-C24/2 | ALTMD-H24/2 | ALTMD-C36/2 | ALTMD-H36/2 | ALTMD-C48/2 | ALTMD-H48/2 | ALTMD-C60/2 | ALTMD-H60/2 | ALTMD-C48/6 | ALTMD-H48/6 | ALTMD-C60/6 | ALTMD-H60/6
|  | Factory Model | ALTHi-18A2/S3 | ALTHi-H18A2/S3 | ALTHi-24A2/S3 | ALTHi-H24A2/S3 | ALTHi-36A2/S3 | ALTHi-H36A2/S3 | ALTHi-48A2/S3 | ALTHi-H48A2/S3 | ALTHi-60A2/S3 | ALTHi-H60A2/S3 | ALTHi-48A6/S3 | ALTHi-H48A6/S3 | ALTHi-60A6/S3 | ALTHi-H60A6/S3
Code |  |  | 65965900410 | 65965900420 | 65970101366 | 65964803170 | 65970101333 | 65970101332 | 65964803140 | 65964803030 | / | 65964803040 | 65970100622 | / | 65964803260 | /
Power Supply |  | V~,Hz,Ph | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 380,60,3 | 380,60,3 | 380,60,3 | 380,60,3
Capacity | Cooling | Btu/h | 18000 | 18000 | 24000 | 24000 | 36000 | 36000 | 48000 | 48000 | 58000 | 58000 | 48000 | 48000 | 55000 | 55000
|  | TR | 1.5 | 1.5 | 2.0387 | 2.0387 | 3 | 3 | 3.9942 | 3.9942 | 5 | 5 | 3.9942 | 3.9942 | 4.6 | 4.6
|  | kW | 5.2 | 5.2 | 7.1 | 7.1 | 10.5 | 10.5 | 14.064 | 14.064 | 15.9978 | 15.9978 | 14.064 | 14.064 | 15.9978 | 15.9978
| Heating | Btu/h | / | 19000 | / | 27000 | / | 37500 | / | 50000 | / | 60000 | / | 50000 | / | 60000
|  | TR | / | 1.5893 | / | 2.2 | / | 3.1204 | / | 4.1845 | / | 5.1 | / | 4.1845 | / | 5.1
|  | kW | / | 5.5963 | / | 7.9086 | / | 10.9875 | / | 14.6456 | / | 17.5 | / | 14.6456 | / | 17.5
Electric Data | Cooling Power Input | kW | 1.9 | 1.9 | 2.81 | 2.81 | 3.98 | 3.98 | 5.25 | 5.25 | 6.25 | 6.25 | 5.21 | 5.21 | 6.8 | 6.8
| Heating Power Input | kW | / | 1.75 | / | 2.86 | / | 3.47 | / | 5.15 | / | 5.86 | / | 5.46 | / | 6.68
| Cooling Current | A | 8.73 | 8.73 | 13.1 | 13.1 | 18.14 | 18.14 | 24.94 | 24.94 | 28.5 | 28.5 | 8.77 | 8.77 | 10.8 | 10.8
| Heating Current | A | / | 8.11 | / | 13.8 | / | 16.2 | / | 23.2 | / | 26.6 | / | 8.14 | / | 9.96
Performance | EER | W/W | 2.7766 | 2.7766 | 2.5032 | 2.5032 | 2.651 | 2.651 | 2.6796 | 2.6796 | 2.7198 | 2.7198 | #REF! | #REF! | #REF! | #REF!
|  | (Btu/h)/W | 9.4737 | 9.4737 | 8.5409 | 8.5409 | 9.0452 | 9.0452 | 9.1429 | 9.1429 | 9.28 | 9.28 | #REF! | #REF! | #REF! | #REF!
| COP | W/W | / | 3.182 | / | 2.7669 | / | 3.1673 | / | 2.8455 | / | 3.0009 | / | #REF! | / | #REF!
|  | (Btu/h)/W | / | 10.8571 | / | 9.4406 | / | 10.8069 | / | 9.7087 | / | 10.2389 | / | #REF! | / | #REF!
Indoor Fan Motor | Model |  | YSK100-4 | YSK100-4 | YSK160-4 | YSK160-4 | YSK180-4 | YSK180-4 | YSK180-4 | YSK180-4 | YSK180-4 | YSK180-4 | YSK180-4 | YSK180-4 | YSK180-4 | YSK180-4
| Brand |  | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO
| Output Power | W | 100 | 100 | 160 | 160 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
| Capacitor | uF | 3 | 3 | 2.5 | 2.5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Speed (Hi/Mi/Lo) | r/min | 960/860/840 | 960/860/840 | 1050/1000/910 | 1050/1000/910 | 1050/1000/910 | 1050/1000/910 | 1100/990/920 | 1100/990/920 | 1100/990/920 | 1100/990/920 | 1100/990/920 | 1100/990/920 | 1100/990/920 | 1100/990/920
Indoor Coil | a.Number Of Row |  | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
| c.Fin Spacing | mm | 1.5 | 1.5 | 1.6 | 1.6 | 1.5 | 1.5 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| d.Fin Material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| e.Tube Outside Dia.And Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
| f.Coil Length x Height x Width | mm | 625×369×25.4 | 625×369×25.4 | 625×369×38.1 | 625×369×38.1 | 625×369×38.1 | 625×369×38.1 | 985×369×38.1 | 985×369×38.1 | 985×369×38.1 | 985×369×38.1 | 985×369×38.1 | 985×369×38.1 | 985×369×38.1 | 985×369×38.1
| g.Number Of U-Tube |  | 18 | 18 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
| h. Number Of Circuits |  | 3 | 3 | 5 | 5 | 5 | 5 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| i.Heat Exchanging Area | m2 | 6.9626 | 6.9626 | 9.8407 | 9.8407 | 10.444 | 10.444 | 15.5587 | 15.5587 | 15.5587 | 15.5587 | 15.5587 | 15.5587 | 15.5587 | 15.5587
Indoor Unit | Indoor Air Flow (Hi/Mi/Lo) | m3/h | 950/760/665 | 950/760/665 | 1200/960/840 | 1200/960/840 | 1500/1200/1050 | 1500/1200/1050 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400
| Rated Input Power(Cooling/Heating) | W | 149 | 149 | 214 | 214 | 260 | 260 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316
| Rated Current (Cooling/Heating) | A | 0.67727 | 0.67727 | 0.97273 | 0.97273 | 1.1818 | 1.1818 | 1.4364 | 1.4364 | 1.4364 | 1.4364 | 1.4364 | 1.4364 | 1.4364 | 1.4364
| Moisture Removal | (L/h) | 1.5 | 1.5 | 2.1 | 2.1 | 3 | 3 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1
| Noise Level(Hi/Mi/Lo) | dB(A) | 44/41/35 | 44/41/35 | 47/44/38 | 47/44/38 | 50/47/41 | 50/47/41 | 53/50/44 | 53/50/44 | 53/50/44 | 53/50/44 | 53/50/44 | 53/50/44 | 53/50/44 | 53/50/44
| Extemal Static Pressure | Pa | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80
| Unit Dimension (W*H*D) | mm | 890×290×785 | 890×290×785 | 890×290×785 | 890×290×785 | 890×290×785 | 890×290×785 | 1250×290×785 | 1250×290×785 | 1250×290×785 | 1250×290×785 | 1250×290×785 | 1250×290×785 | 1250×290×785 | 1250×290×785
| Packing (W*H*D) | mm | 1100×360×870 | 1100×360×870 | 1100×360×870 | 1100×360×870 | 1100×360×870 | 1100×360×870 | 1460×360×870 | 1460×360×870 | 1460×360×870 | 1460×360×870 | 1460×360×870 | 1460×360×870 | 1460×360×870 | 1460×360×870
| Net Weight | Kg | 34 | 34 | 36 | 36 | 36 | 36 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
| Gross Weight | Kg | 40 | 40 | 42 | 42 | 42 | 42 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59
Refrigerant Pipe | Liquid Side | mm | φ6.35 | φ6.35 | φ9.52 | φ9.52 | 9.52 | 9.52 | φ9.52 | φ9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
| Gas Side | mm | φ12.7 | φ12.7 | φ15.88 | φ15.88 | 15.88 | 15.88 | φ19.05 | φ19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24
Application Area |  | m2 | 21-35 | 21-35 | 28-47 | 28-47 | 42-70 | 42-70 | 56-93 | 56-93 | 64-107 | 64-107 | 56-93 | 56-93 | 64-107 | 64-107
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2
| Power Wiring( Outdoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×4mm2 | 3×4mm2 | 3×10mm2 | 3×10mm2 | 3×10mm2 | 3×10mm2 | 3×12mm2 | 3×12mm2 | 5×4mm2 | 5×4mm2 | 5×4mm2 | 5×4mm2
| Signal Wiring | mm2 | / | 2×1mm2 | / | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Wired Controller |  |  | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 46/95/115 | 46/95/115 | 44/92/112 | 44/92/112 | 36/75/88 | 36/75/88 | 25/52/54 | 25/52/54 | 25/52/54 | 25/52/54 | 25/52/54 | 25/52/54 | 25/52/54 | 25/52/54
Remark:The above designs and specifications are subject to change of product improvement without prior notice.

## T3 60Hz HD (hidden)
Return |  | Model | ALTHD-C24/2 | ALTHD-H24/2 | ALTHD-C36/2 | ALTHD-H36/2 | ALTHD-C48/2 | ALTHD-H48/2 | ALTHD-C60/2 | ALTHD-H60/2 | ALTHD-C48/6 | ALTHD-H48/6 | ALTHD-C60/6 | ALTHD-H60/6
|  | Factory Model | ALHi-24A2/B | ALHi-H24A2/B | ALHi-36A2/B | ALHi-H36A2/B | ALHi-48A2/B | ALHi-H48A2/B | ALHi-60A2/B | ALHi-H60A2/B | ALHi-48A6/B | ALHi-H36A6/B | ALHi-60A6/B | ALHi-H60A6/B
Power Supply |  | V~,Hz,Ph | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 380,60,3 | 380,60,3 | 380,60,3 | 380,60,3
Capacity | Cooling | Btu/h | 24000 | 24000 | 36000 | 36000 | 48000 | 48000 | 55000 | 55000 | 48000 | 48000 | 55000 | 55000
|  | TR | 2.0387 | 2.0387 | 3 | 3 | 3.9942 | 3.9942 | 4.6 | 4.6 | 3.9942 | 3.9942 | 4.6 | 4.6
|  | kW | 7.1 | 7.1 | 10.5 | 10.5 | 14.1 | 14.1 | 15.9978 | 15.9978 | 14.1 | 14.1 | 15.9978 | 15.9978
| Heating | Btu/h | / | 27000 | / | 37500 | / | 51000 | / | 60000 | / | 49700 | / | 60000
|  | TR | / | 2.2 | / | 3.1204 | / | 4.3 | / | 5.1 | / | 4.1845 | / | 5.1
|  | kW | / | 7.9086 | / | 10.9875 | / | 15 | / | 17.5 | / | 14.6456 | / | 17.5
Electric Data | Cooling Power Input | kW | 2.81 | 2.81 | 3.98 | 3.98 | 5.25 | 5.25 | 6.25 | 6.25 | 5.21 | 5.21 | 6.8 | 6.8
| Heating Power Input | kW | / | 2.86 | / | 3.47 | / | 5.15 | / | 5.86 | / | 5.46 | / | 6.68
| Cooling Current | A | 13.1 | 13.1 | 18.14 | 18.14 | 24.94 | 24.94 | 28.5 | 28.5 | 8.77 | 8.77 | 10.8 | 10.8
| Heating Current | A | / | 13.8 | / | 16.2 | / | 23.2 | / | 26.6 | / | 8.14 | / | 9.96
Performance | EER | W/W | 2.5032 | 2.5032 | 2.651 | 2.651 | 2.6796 | 2.6796 | 2.5791 | 2.5791 | 2.7002 | 2.7002 | 2.3705 | 2.3705
|  | (Btu/h)/W | 8.5409 | 8.5409 | 9.0452 | 9.0452 | 9.1429 | 9.1429 | 8.8 | 8.8 | 9.2131 | 9.2131 | 8.0882 | 8.0882
| COP | W/W | / | 2.7669 | / | 3.1673 | / | 2.9024 | / | 3.0009 | / | 2.6678 | / | 2.6325
|  | (Btu/h)/W | / | 9.4406 | / | 10.8069 | / | 9.9029 | / | 10.2389 | / | 9.1026 | / | 8.982
Indoor Fan Motor | Model |  | YDK200-4 | YDK200-4 | YDK200-4 | YDK200-4 | YDK200-4 | YDK200-4 | YDK200-4 | YDK200-4 | YDK200-4 | YDK200-4 | YDK200-4 | YDK200-4
| Brand |  | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO
| Output Power | W | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Capacitor | uF | 10μF/450V a.c | 10μF/450V a.c | 10μF/450V a.c | 10μF/450V a.c | 10μF/450V a.c | 10μF/450V a.c | 10μF/450V a.c | 10μF/450V a.c | 10μF/450V a.c | 10μF/450V a.c | 10μF/450V a.c | 10μF/450V a.c
| Speed (Hi/Mi/Lo) | r/min | 1150/1220/1371 | 1150/1220/1371 | 1150/1220/1371 | 1150/1220/1371 | 1150/1220/1371 | 1150/1220/1371 | 1150/1220/1371 | 1150/1220/1371 | 1150/1220/1371 | 1150/1220/1371 | 1150/1220/1371 | 1150/1220/1371
Indoor Coil | a.Number Of Row |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| b.Tube Pitch(a)x Row Pitch(b) | mm | 19.05×22 | 19.05×22 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 19.05×22 | 19.05×22 | 20.5×12.7 | 20.5×12.7 | 19.05×22 | 19.05×22
| c.Fin Spacing | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| d.Fin Material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| e.Tube Outside Dia.And Material | mm | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved
| f.Coil Length x Height x Width | mm | 582×60×352 | 582×60×352 | 930×57×328 | 930×57×328 | 930×57×328 | 930×57×328 | 930×60×352 | 930×60×352 | 930×57×328 | 930×57×328 | 930×60×352 | 930×60×352
| g.Number Of U-Tube |  | 20 | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| h. Number Of Circuits |  | 4 | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
| i.Heat Exchanging Area | m2 | 11.32 | 11.32 | 13.4 | 13.4 | 13.4 | 13.4 | 15.89 | 15.89 | 15.5587 | 15.5587 | 15.89 | 15.89
Indoor Unit | Indoor Air Flow (Hi/Mi/Lo) | m3/h | 1200/960/840 | 1200/960/840 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400
| Rated Input Power(Cooling/Heating) | W | 7200 | 7200 | 10500 | 10500/11550 | 14000 | 14000/15000 | 16000 | 16000/16500 | 14000 | 14000/15000 | 16000 | 16000/16500
| Rated Current (Cooling/Heating) | A | 12.95/12.15 | 12.95/12.15 | 7.7 | 7.7/7.38 | 10.4 | 10.40/10.34 | 12.78 | 12.78/12.55 | 10.4 | 10.40/10.34 | 12.78 | 12.78/12.55
| Moisture Removal | (L/h) | / | / | / | / | / | / | / | / | / | / | / | /
| Noise Level(Hi/Mi/Lo) | dB(A) | 53/50/44 | 53/50/44 | 60/57/51 | 60/57/51 | 60/57/51 | 60/57/51 | 60/57/51 | 60/57/51 | 60/57/51 | 60/57/51 | 60/57/51 | 60/57/51
| Extemal Static Pressure | Pa | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196 | 196
| Unit Dimension (W*H*D) | mm | 852×719×380 | 852×719×380 | 1200×719×380 | 1200×719×380 | 1200×719×380 | 1200×719×380 | 1200×719×380 | 1200×719×380 | 1200×719×380 | 1200×719×380 | 1200×719×380 | 1200×719×380
| Packing (W*H*D) | mm | 885×760×415 | 885×760×415 | 1235×760×415 | 1235×760×415 | 1235×760×415 | 1235×760×415 | 1235×760×415 | 1235×760×415 | 1235×760×415 | 1235×760×415 | 1235×760×415 | 1235×760×415
| Net Weight | Kg | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
| Gross Weight | Kg | 37 | 37 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
Refrigerant Pipe | Liquid Side | mm | φ9.52 | φ9.52 | 9.52 | 9.52 | φ9.52 | φ9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
| Gas Side | mm | φ15.88 | φ15.88 | 15.88 | 15.88 | φ19.05 | φ19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24
Application Area |  | m2 | 28-47 | 28-47 | 42-70 | 42-70 | 56-93 | 56-93 | 64-107 | 64-107 | 56-93 | 56-93 | 64-107 | 64-107
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2
| Power Wiring( Outdoor) | mm2 | 3×4mm2 | 3×4mm2 | 3×10mm2 | 3×10mm2 | 3×10mm2 | 3×10mm2 | 3×12mm2 | 3×12mm2 | 5×4mm2 | 5×4mm2 | 5×4mm2 | 5×4mm2
| Signal Wiring | mm2 | / | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Wired Controller |  |  | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 44/92/112 | 44/92/112 | 36/75/88 | 36/75/88 | 25/52/54 | 25/52/54 | 25/52/54 | 25/52/54 | 25/52/54 | 25/52/54 | 25/52/54 | 25/52/54
Remark:The above designs and specifications are subject to change of product improvement without prior notice.

## T3 60Hz LD (hidden)
Return |  | Model | ALTLD-C18/2 | ALTLD-H18/2 | ALTLD-C24/2 | ALTLD-H24/2
|  | Factory Model | ALTDu-18A2/S3 | ALTDu-H18A2/S3 | ALTDu-24A2/S3 | ALTDu-H24A2/S3
Code |  |  | 65964803220 | 65970100072 | 65964803230 | 65970900073
Power Supply |  | V~,Hz,Ph | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1
Capacity | Cooling | Btu/h | 18000 | 18000 | 24000 | 24000
|  | TR | 1.5 | 1.5 | 2.0387 | 2.0387
|  | kW | 5.2 | 5.2 | 7.1 | 7.1
| Heating | Btu/h | / | 19000 | / | 27000
|  | TR | / | 1.5893 | / | 2.2596
|  | kW | / | 5.5963 | / | 7.9086
Electric Data | Cooling Power Input | kW | 1.9 | 1.9 | 2.81 | 2.81
| Heating Power Input | kW | / | 1.75 | / | 2.86
| Cooling Current | A | 8.73 | 8.73 | 13.1 | 13.1
| Heating Current | A | / | 8.11 | / | 13.8
Performance | EER | W/W | 2.7368 | 2.7368 | 2.5267 | 2.5267
|  | (Btu/h)/W | 9.4737 | 9.4737 | 8.5409 | 8.5409
| COP | W/W | / | 3.1979 | / | 2.7652
|  | (Btu/h)/W | / | 10.8571 | / | 9.4406
Indoor Fan Motor | Model |  | YSK30-4 | YSK30-4 | YSK50-4 | YSK50-4
| Brand |  | KANGBAO | KANGBAO | KANGBAO | KANGBAO
| Output Power | W | 30 | 30 | 50 | 50
| Capacitor | uF | 1.5 | 1.5 | 2 | 2
| Speed (Hi/Mi/Lo) | r/min | 810/730/680 | 810/730/680 | 960/810/720 | 960/810/720
Indoor Coil | a.Number Of Row |  | 3 | 3 | 3 | 3
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
| c.Fin Spacing | mm | 1.6 | 1.6 | 1.6 | 1.6
| d.Fin Material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| e.Tube Outside Dia.And Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
| f.Coil Length x Height x Width | mm | 920×205×38.1 | 920×205×38.1 | 1110×205×38.1 | 1110×205×38.1
| g.Number Of U-Tube |  | 15 | 15 | 15 | 15
| h. Number Of Circuits |  | 5 | 5 | 5 | 5
| i.Heat Exchanging Area | m2 | 8.07 | 8.07 | 9.74 | 9.74
Indoor Unit | Indoor Air Flow (Hi/Mi/Lo) | m3/h | 860/688/602 | 860/688/602 | 1200/960/840 | 1200/960/840
| Rated Input Power(Cooling/Heating) | W | 110 | 110 | 150 | 150
| Rated Current (Cooling/Heating) | A | 0.39 | 0.39 | 0.57 | 0.57
| Moisture Removal | (L/h) | 1.5 | 1.5 | 2.1 | 2.1
| Noise Level(Hi/Mi/Lo) | dB(A) | 42/39/34 | 42/39/34 | 45/42/36 | 45/42/36
| Extemal Static Pressure | Pa | 12/30 | 12/30 | 12/30 | 12/30
| Unit Dimension (W*H*D) | mm | 880x547x240 | 880x547x240 | 1305x547x240 | 1305x547x240
| Packing (W*H*D) | mm | 980x620x280 | 980x620x280 | 1400x620x280 | 1400x620x280
| Net Weight | Kg | 30 | 30 | 34.5 | 34.5
| Gross Weight | Kg | 34 | 34 | 39.5 | 39.5
Refrigerant Pipe | Liquid Side | mm | 6.35 | 6.35 | 9.52 | 9.52
| Gas Side | mm | 12.7 | 12.7 | 15.88 | 15.88
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24
Application Area |  | m2 | 21-35 | 21-35 | 28-47 | 28-47
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×1mm2 | 3×1mm2
| Power Wiring( Outdoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×4mm2 | 3×4mm2
| Signal Wiring | mm2 | / | 2×1mm2 | / | 4×1mm2
Wired Controller |  |  | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3 | G-XK-HCE3
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 60/134/158 | 60/134/158 | 54/111/126 | 54/111/126
Remark:The above designs and specifications are subject to change of product improvement without prior notice.

## T3 60Hz R22 Ca (hidden)
Return |  | Model | ALTCA-C18/2 | ALTCA-H18/2 | ALTCA-C24/2 | ALTCA-H24/2 | ALTCA-C36/2 | ALTCA-H36/2 | ALTCA-C48/2 | ALTCA-H48/2 | ALTCA-C48/9 | ALTCA-H48/9
|  | Factory Model | ALTCa-18A2/C7 | ALTCa-H18A2/C7 | ALTCa-24A2/C7 | ALTCa-H24A2/C7 | ALTCa-36A2/C7 | ALTCa-H36A2/C7 | ALTCa-48A2/C7 | ALTCa-H48A2/C7 | ALTCa-48A9/C7 | ALTCa-H48A9/C7
Code |  |  | 65970101329 | 65970101330 | 65971000534 | 65971000120 | 65971000567 | 65970101331 | 65971000570 | 65971000191 | / | /
Power Supply |  | V~,Hz,Ph | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 380,60,3 | 380,60,3
Capacity | Cooling | Btu/h | 18000 | 18000 | 24000 | 24000 | 36000 | 36000 | 48000 | 48000 | 48000 | 48000
|  | TR | 1.5 | 1.5 | 2.0387 | 2.0387 | 3 | 3 | 3.9942 | 3.9942 | 3.9942 | 3.9942
|  | kW | 5.2 | 5.2 | 7.1 | 7.1 | 10.5 | 10.5 | 14.064 | 14.064 | 14.064 | 14.064
| Heating | Btu/h | / | 19000 | / | 27000 | / | 37500 | / | 50000 | / | 50000
|  | TR | / | 1.5893 | / | 2.2596 | / | 3.1204 | / | 4.1845 | / | 4.1845
|  | kW | / | 5.5963 | / | 7.9086 | / | 10.9875 | / | 14.6456 | / | 14.6456
Electric Data | Cooling Power Input | kW | 1.9 | 1.9 | 2.81 | 2.81 | 3.98 | 3.98 | 5.25 | 5.25 | 5.25 | 5.21
| Heating Power Input | kW | / | 1.75 | / | 2.86 | / | 3.47 | / | 5.15 | / | 5.46
| Cooling Current | A | 8.73 | 8.73 | 13.1 | 13.1 | 18.14 | 18.14 | 24.94 | 24.94 | 15.7 | 15.7
| Heating Current | A | / | 8.11 | / | 13.8 | / | 16.2 | / | 23.2 | / | 15.4
Performance | EER | W/W | 2.7766 | 2.7766 | 2.5032 | 2.5032 | 2.651 | 2.651 | 2.6796 | 2.6796 | 2.6789 | 2.6789
|  | (Btu/h)/W | 9.4737 | 9.4737 | 8.5409 | 8.5409 | 9.0452 | 9.0452 | 9.1429 | 9.1429 | 9.1429 | 9.1429
| COP | W/W | / | 3.182 | / | 2.7669 | / | 3.1673 | / | 2.8455 | / | 2.8438
|  | (Btu/h)/W | / | 10.8571 | / | 9.4406 | / | 10.8069 | / | 9.7087 | / | 9.7087
Indoor Fan Motor | Model |  | YDK30-6E | YDK30-6E | YDK30-6 Q | YDK30-6 Q | YDK45-6 Q | YDK45-6 Q | YDK80-8-60 Q | YDK80-8-60 Q | YDK80-8-60 Q | YDK80-8-60 Q
| Brand |  | HAICHENG | HAICHENG | HUATE | HUATE | HUATE | HUATE | WEILING | WEILING | WEILING | WEILING
| Output Power | W | 25 | 25 | 30 | 30 | 45 | 45 | 80 | 80 | 80 | 80
| Capacitor | uF | 2.5 | 2.5 | 3 | 3 | 4 | 4 | 6 | 6 | 6 | 6
| Speed (Hi/Mi/Lo) | r/min | 920/850/750 | 920/850/750 | 500/400/320 | 500/400/320 | 650/520/450 | 650/520/450 | 685/540/450 | 685/540/450 | 685/540/450 | 685/540/450
Indoor Coil | a.Number Of Row |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
| c.Fin Spacing | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| d.Fin Material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| e.Tube Outside Dia.And Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
| f.Coil Length x Height x Width | mm | 1115×205×25.4 | 1115×205×25.4 | 2142×205×25.4 | 2142×205×25.4 | 2142×205×25.4 | 2142×205×25.4 | 2142×246×25.4 | 2142×246×25.4 | 2142×246×25.4 | 2142×246×25.4
| g.Number Of U-Tube |  | 9 | 9 | 8 | 8 | 9 | 9 | 11 | 11 | 11 | 11
| h. Number Of Circuits |  | 4 | 4 | 8 | 8 | 9 | 9 | 11 | 11 | 11 | 11
| i.Heat Exchanging Area | m2 | 7.0887 | 7.0887 | 10.025 | 10.025 | 12.7597 | 12.7597 | 15.5952 | 15.5952 | 15.5952 | 15.5952
Indoor Unit | Indoor Air Flow (Hi/Mi/Lo) | m3/h | 850/680/595 | 850/680/595 | 1100/880/770 | 1100/880/770 | 1500/1200/1050 | 1500/1200/1050 | 1800/1440/1260 | 1800/1440/1260 | 1800/1440/1260 | 1800/1440/1260
| Rated Input Power(Cooling/Heating) | W | 63 | 63 | 73 | 73 | 94 | 94 | 145 | 145 | 145 | 145
| Rated Current (Cooling/Heating) | A | 0.28636 | 0.28636 | 0.33182 | 0.33182 | 0.42727 | 0.42727 | 0.65909 | 0.65909 | 0.65909 | 0.65909
| Moisture Removal | (L/h) | 1.5 | 1.5 | 2.1 | 2.1 | 3 | 3 | 5.1 | 5.1 | 5.1 | 5.1
| Noise Level(Hi/Mi/Lo) | dB(A) | 41/38/32 | 41/38/32 | 45/42/36 | 45/42/36 | 48/45/39 | 48/45/39 | 50/47/41 | 50/47/41 | 50/47/41 | 50/47/41
| Extemal Static Pressure | Pa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unit Dimension (W*H*D) | mm | 615×615×263 | 615×615×263 | 835x240x835 | 835x240x835 | 835x240x835 | 835x240x835 | 835x280x835 | 835x280x835 | 835x280x835 | 835x280x835
| Packing (W*H*D) | mm | 700×700×330 | 700×700×330 | 900x320x900 | 900x320x900 | 900x320x900 | 900x320x900 | 900x360x900 | 900x360x900 | 900x360x900 | 900x360x900
| Net Weight | Kg | 20 | 20 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30
| Gross Weight | Kg | 25 | 25 | 34 | 34 | 34 | 34 | 37 | 37 | 37 | 37
Panel | Unit Dimension (W*H*D) | mm | 650×55×650 | 650×55×650 | 950×55×950 | 950×55×950 | 950×55×950 | 950×55×950 | 950×55×950 | 950×55×950 | 950×55×950 | 950×55×950
| Packing (W*H*D) | mm | 700×70×700 | 700×70×700 | 1000×100×1000 | 1000×100×1000 | 1000×100×1000 | 1000×100×1000 | 1000×100×1000 | 1000×100×1000 | 1000×100×1000 | 1000×100×1000
| Net Weight | Kg | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| Gross Weight | Kg | 5 | 5 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Refrigerant Pipe | Liquid Side | mm | φ6.35 | φ6.35 | φ9.52 | φ9.52 | φ9.52 | φ9.52 | φ9.52 | φ9.52 | φ9.52 | φ9.52
| Gas Side | mm | φ12.7 | φ12.7 | φ15.88 | φ15.88 | φ15.88 | φ15.88 | φ19.05 | φ19.05 | φ19.05 | φ19.05
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24
Application Area |  | m2 | 21-35 | 21-35 | 28-47 | 28-47 | 42-70 | 42-70 | 56-93 | 56-93 | 56-93 | 56-93
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2
| Power Wiring( Outdoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×4mm2 | 3×4mm2 | 3×10mm2 | 3×10mm2 | 3×10mm2 | 3×10mm2 | 5×4mm2 | 5×4mm2
| Signal Wiring | mm2 | / | 2×1mm2 | / | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 2×1mm2
Drainage Water Pipe Dia. |  | mm | 26 | 26 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
Wireless Remote Controller |  |  | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 51/112/120 | 51/112/120 | 40/86/98 | 40/86/98 | 34/70/78 | 34/70/78 | 24/54/54 | 24/54/54 | 24/54/54 | 24/54/54
Remark:The above designs and specifications are subject to change of product improvement without prior notice.

## T3 60Hz R22 CF (hidden)
Return |  | Model | ALTCF-C18/2 | ALTCF-H18/2 | ALTCF-C24/2 | ALTCF-H24/2 | ALTCF-C36/2 | ALTCF-H36/2 | ALTCF-C48/2 | ALTCF-H48/2 | ALTCF-C60/2 | ALTCF-H60/2 | ALTCF-C48/9 | ALTCF-H48/9 | ALTCF-C60/9 | ALTCF-H60/9
|  | Factory Model | ALTCe-18A2/C5 | ALTCe-H18A2/C5 | ALTCe-24A2/C5 | ALTCe-H24A2/C5 | ALTCe-36A2/C5 | ALTCe-H36A2/C5 | ALTCe-48A2/C5 | ALTCe-H48A2/C5 | ALTCe-60A2/C5 | ALTCe-H602/C5 | ALTCe-48A9/C5 | ALTCe-H48A9/C5 | ALTCe-60A9/C5 | ALTCe-H60A9/C5
Code |  |  | / | 65970100612 | 65970101386 | 65970100613 | 65970101385 | 65970100614 | 65970101279 | 65970101384 | / | 65970100615 | / | / | / | /
Power Supply |  | V~,Hz,Ph | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,1 | 208~230,60,3 | 208~230,60,3 | 208~230,60,3 | 208~230,60,3
Capacity | Cooling | Btu/h | 18000 | 18000 | 24000 | 24000 | 36000 | 36000 | 48000 | 48000 | 55000 | 55000 | 48000 | 48000 | 55000 | 55000
|  | TR | 1.5 | 1.5 | 2.0387 | 2.0387 | 3 | 3 | 3.9942 | 3.9942 | 4.6 | 4.6 | 3.9942 | 3.9942 | 4.6 | 4.6
|  | kW | 5.2 | 5.2 | 7.1 | 7.1 | 10.5 | 10.5 | 14.064 | 14.064 | 16 | 16 | 14.064 | 14.064 | 16 | 16
| Heating | Btu/h | / | 19000 | / | 27000 | / | 37500 | / | 50000 | / | 60000 | / | 50000 | / | 60000
|  | TR | / | 1.5893 | / | 2.2596 | / | 3.1204 | / | 4.1845 | / | 5.1 | / | 4.1845 | / | 5.1
|  | kW | / | 5.5963 | / | 7.9086 | / | 11 | / | 14.6456 | / | 17.5 | / | 14.6456 | / | 17.5
Electric Data | Cooling Power Input | kW | 1.9 | 1.9 | 2.81 | 2.81 | 3.98 | 3.98 | 5.25 | 5.25 | 5.88 | 5.88 | 5.25 | 5.25 | 5.88 | 5.88
| Heating Power Input | kW | / | 1.75 | / | 2.86 | / | 3.47 | / | 5.15 | / | 5.85 | / | 5.15 | / | 5.85
| Cooling Current | A | 8.73 | 8.73 | 13.1 | 13.1 | 18.14 | 18.14 | 24.94 | 24.94 | 26.8235 | 26.8235 | 15.7 | 15.7 | 19.1059 | 19.1059
| Heating Current | A | / | 8.11 | / | 13.8 | / | 16.2 | / | 23.2 | / | 26.5675 | / | 15.4 | / | 19.8757
Performance | EER | W/W | 2.7368 | 2.7368 | 2.5267 | 2.5267 | 2.6382 | 2.6382 | 2.6789 | 2.6789 | 2.72 | 2.72 | 2.6789 | 2.6789 | 2.72 | 2.72
|  | (Btu/h)/W | 9.4737 | 9.4737 | 8.5409 | 8.5409 | 9.0452 | 9.0452 | 9.1429 | 9.1429 | 9.28 | 9.28 | 9.1429 | 9.1429 | 9.28 | 9.28
| COP | W/W | / | 3.1979 | / | 2.7558 | / | 3.1664 | / | 2.9126 | / | 2.9863 | / | 2.6671 | / | 2.9863
|  | (Btu/h)/W | / | 10.8571 | / | 9.4056 | / | 10.8069 | / | 9.9417 | / | 10.2389 | / | 9.3773 | / | 10.2389
Indoor Fan Motor | Model |  | YSK-40W-4 | YSK-40W-4 | YSK-60W-4 | YSK-60W-4 | YSK-70W-4 | YSK-70W-4 | YSK-105W-4 | YSK-105W-4 | YSK-105W-4 | YSK-105W-4 | YSK-105W-4 | YSK-105W-4 | YSK-105W-4 | YSK-105W-4
| Brand |  | HUATE | HUATE | HUATE | HUATE | HUATE | HUATE | HUATE | HUATE | HUATE | HUATE | HUATE | HUATE | HUATE | HUATE
| Output Power | W | 40 | 40 | 60 | 60 | 70 | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
| Capacitor | uF | 2.5 | 2.5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Speed (Hi/Mi/Lo) | r/min | 1250/1000/875 | 1250/1000/875 | 1400/1100/990 | 1400/1100/990 | 1380/1100/970 | 1380/1100/970 | 1380/1100/970 | 1380/1100/970 | 1380/1100/970 | 1380/1100/970 | 1380/1100/970 | 1380/1100/970 | 1380/1100/970 | 1380/1100/970
Indoor Coil | a.Number Of Row |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 22×19.05 | 22×19.05 | 25.4×22 | 25.4×22 | 22×19.05 | 22×19.05 | 25.4×22 | 25.4×22 | 22×19.05 | 22×19.05
| c.Fin Spacing | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| d.Fin Material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| e.Tube Outside Dia.And Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved
| f.Coil Length x Height x Width | mm | 570×246×38.1 | 570×246×38.1 | 570×246×38.1 | 570×242×57.15 | 950×242×57.15 | 950×242×57.15 | 1333×220×38.1 | 1333×220×38.1 | 1333×242×57.15 | 1333×242×57.15 | 1333×220×38.1 | 1333×220×38.1 | 1333×242×57.15 | 1333×242×57.15
| g.Number Of U-Tube |  | 18 | 18 | 16 | 16 | 16 | 16 | 10 | 10 | 16 | 16 | 10 | 10 | 16 | 16
| h. Number Of Circuits |  | 3 | 3 | 6 | 6 | 6 | 6 | 5 | 5 | 6 | 6 | 5 | 5 | 6 | 6
| i.Heat Exchanging Area | m2 | 6 | 6 | 8.74 | 8.74 | 14.56 | 14.56 | 16.36 | 16.36 | 19.93 | 19.93 | 16.36 | 16.36 | 19.93 | 19.93
Indoor Unit | Indoor Air Flow (Hi/Mi/Lo) | m3/h | 850/680/595 | 850/680/595 | 1200/960/840 | 1200/960/840 | 1500/1200/1050 | 1500/1200/1050 | 1800/1440/1260 | 1800/1440/1260 | 1800/1440/1260 | 1800/1440/1260 | 1800/1440/1260 | 1800/1440/1260 | 1800/1440/1260 | 1800/1440/1260
| Rated Input Power(Cooling/Heating) | W | 40 | 40 | 50 | 50 | 65 | 65 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
| Rated Current (Cooling/Heating) | A | 0.18182 | 0.18182 | 0.22727 | 0.22727 | 0.29545 | 0.29545 | 0.47727 | 0.47727 | 0.47727 | 0.47727 | 0.47727 | 0.47727 | 0.47727 | 0.47727
| Moisture Removal | (L/h) | 1.5 | 1.5 | 2.1 | 2.1 | 3 | 3 | 5.1 | 5.1 | 5.5 | 5.5 | 5.1 | 5.1 | 5.5 | 5.5
| Noise Level(Hi/Mi/Lo) | dB(A)
| Extemal Static Pressure | Pa | 43/40/34 | 43/40/34 | 46/43/37 | 46/43/37 | 50/47/41 | 50/47/41 | 51/48/42 | 51/48/42 | 51/48/42 | 51/48/42 | 51/48/42 | 51/48/42 | 51/48/42 | 51/48/42
| Unit Dimension (W*H*D) | mm | 929x660x205 | 929x660x205 | 929x660x205 | 929x660x205 | 1280x660x205 | 1280x660x205 | 1631x660x205 | 1631x660x205 | 1631x660x205 | 1631x660x205 | 1631x660x205 | 1631x660x205 | 1631x660x205 | 1631x660x205
| Packing (W*H*D) | mm | 1000x710x280 | 1000x710x280 | 1000x710x280 | 1000x710x280 | 1350x710x280 | 1350x710x280 | 1700x710x280 | 1700x710x280 | 1700x710x280 | 1700x710x280 | 1700x710x280 | 1700x710x280 | 1700x710x280 | 1700x710x280
| Net Weight | Kg | 25 | 25 | 26 | 26 | 33 | 33 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
| Gross Weight | Kg | 28 | 28 | 28 | 28 | 38 | 38 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
Refrigerant Pipe | Liquid Side | mm | 6.35 | 6.35 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
| Gas Side | mm | 12.7 | 12.7 | 15.88 | 15.88 | 15.88 | 15.88 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05
Operation Temperature Range |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient Temperature Range(Cooling/Heating) |  | ℃ | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24 | 17~54 | 17~54/-5~24
Application Area |  | m2 | 21-35 | 21-35 | 28-47 | 28-47 | 42-70 | 42-70 | 56-93 | 56-93 | 64-107 | 64-107 | 56-93 | 56-93 | 64-107 | 64-107
Connection Wiring | Power Wiring( Indoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2 | 3×1mm2
| Power Wiring( Outdoor) | mm2 | 3×2.5mm2 | 3×2.5mm2 | 3×4mm2 | 3×4mm2 | 3×10mm2 | 3×10mm2 | 3×10mm2 | 3×10mm2 | 3×10mm2 | 3×10mm2 | 5×4mm2 | 5×4mm2 | 5×4mm2 | 5×4mm2
| Signal Wiring | mm2 | / | 2×1mm2 | / | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 4×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2 | 2×1mm2
Wireless Remote Controller |  |  | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E | YKR-H/009E
Qty’per 20’& 40’&40HQ(Only For Reference) |  | Set | 56/134/136 | 56/134/136 | 56/115/115 | 56/115/115 | 36/73/89 | 36/73/89 | 26/56/64 | 26/56/64 | 26/56/64 | 26/56/64 | 26/56/64 | 26/56/64 | 26/56/64 | 26/56/64
Remark:The above designs and specifications are subject to change of product improvement without prior notice.

## T1 50Hz R410A CA (hidden)
Return |  | Model |  | ALCa-H12A4/R1-C5 | ALCa-H18A4/R1-C5 | ALCa-H24B4/R1-C5 | ALCa-H36A5/R1-C5 | ALCa-H42A5/R1-C5 | ALCa-H48A5/R1-C5 | ALCa-H60A5/R1-C5
Power supply |  |  | Ph-V-Hz | 1Ph / 220-240V/50HZ | 1Ph / 220-240V/50HZ | 1Ph / 220-240V/50HZ | 3Ph / 380-415V/50HZ | 3Ph / 380-415V/50HZ | 3Ph / 380-415V/50HZ | 3Ph / 380-415V/50HZ
Cooling |  | Capacity | W | 3600 | 5300 | 7200 | 10600 | 12000 | 14000 | 17600
|  |  | BTU | 12000 | 18000 | 24000 | 36000 | 42000 | 48000 | 60000
|  | Input | W | 1300 | 1940 | 2700 | 3850 | 4600 | 4870 | 6280
|  | Rated current | A | 6 | 8.91 | 12.5 | 6.9 | 8.42 | 8.88 | 11.46
|  | EER |  | 2.7692 | 2.732 | 2.6667 | 2.7532 | 2.6087 | 2.8747 | 2.8025
Heating |  | Capacity | W | 3900 | 5800 | 8080 | 11700 | 14000 | 15500 | 18500
|  |  | BTU | 13200 | 19800 | 26400 | 39600 | 46200 | 52800 | 66000
|  | Input | W | 1220 | 1900 | 2500 | 3500 | 4700 | 5130 | 5970
|  | Rated current | A | 5.72 | 8.73 | 11.59 | 6.28 | 8.56 | 9.33 | 10.83
|  | COP |  | 3.1967 | 3.0526 | 3.232 | 3.3429 | 2.9787 | 3.0214 | 3.0988
Max. input consumption |  |  | W | 1750 | 2650 | 3200 | 4570 | 5800 | 6100 | 7800
Max. current |  |  | A | 7.9545 | 12.0455 | 14.5455 | 12.0263 | 15.2632 | 16.0526 | 20.5263
Compressor |  | Model |  | PA150X2C-4FT | PA215X2CS-4KU1 | PA290X3CS-4MUI | C-SBP130H38A | C-SBP160H38A | C-SBP170H38A | JT170G-P8Y1
|  | Type |  | ROTARY | ROTARY | ROTARY | SCROLL | SCROLL | SCROLL | SCROLL
|  | Brand |  | TOSHIBA | TOSHIBA | TOSHIBA | SANYO | SANYO | SANYO | DAKIN
|  | Capacity | W | 3670 | 5340 | 7180 | 10900 | 13200 | 14100 | 15900
|  | Input | W | 1245 | 1830 | 2430 | 3750 | 4600 | 4750 | 4500
|  | Rated current(RLA) | A | 5.75 | 8.55 | 11.4 | 6.8 | 8.61 | 8.68 | 8.9
|  | Locked rotor Amp(LRA) | A | 29.9 | 36.8 | 61 | 66 | 73 | 63 | 59.4
|  | Thermal protector |  | UP3RE0596-T56 | UP3SE0391-T39 | UP14SE5145 | UP18 | UP18 | UP18 | UP18WA162-46G
|  | Capacitor | uF | 35 | 50 | 50 | / | / | / | /
|  | Refrigerant oil | ml | 480 | 750 | 950 | 1700 | 1700 | 1700 | 1500
Indoor unit | Indoor fan motor | Model |  | YDK10-6 Q | YDK25-6-50 Q | YDK30-6 Q | YDK45-6 Q | YDK80-6-50 Q | YDK80-6-50 Q | YDK80-6-50 Q
|  | Brand |  | HUATE | HUATE | HUATE | HUATE | KANGBAO | KANGBAO | KANGBAO
|  | Output Power | W | 10 | 25 | 30 | 45 | 80 | 80 | 80
|  | Capacitor | uF | 1.5 | 2.5 | 3 | 4 | 6 | 6 | 6
|  | Speed (Hi/Mi/Lo) | r/min | 820/720/590 | 930/750/650 | 500/400/320 | 650/520/450 | 685/540/450 | 685/540/450 | 685/540/450
| Indoor coil | a.Number of row |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | b.Tube pitch(a)x row pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
|  | c.Fin spacing | mm | 1.5 | 1.4 | 1.6 | 1.4 | 1.4 | 1.4 | 1.4
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
|  | f.Coil length x height x width | mm | 1115×205×25.4 | 1115×205×25.4 | 2142×205×25.4 | 2142×205×25.4 | 2142×246×25.4 | 2142×246×25.4 | 2142×246×25.4
|  | g.Number of U-Tube |  | 8 | 10 | 8 | 9 | 11 | 11 | 11
|  | h. Number of circuits |  | 3 | 4 | 8 | 9 | 11 | 11 | 11
|  | i.Heat exchanging area | m2 | 4.846 | 7.0887 | 10.025 | 12.7597 | 15.5952 | 15.5952 | 15.5952
| Indoor air flow (Hi/Mi/Lo) |  | m3/h | 620/496/434 | 850/680/595 | 1100/880/770 | 1500/1200/1050 | 1700/1360/1190 | 1700/1360/1190 | 1700/1360/1190
| Rated input Power(cooling/heating) |  | W | 25 | 63 | 73 | 94 | 145 | 145 | 145
| Rated current (cooling/heating) |  | A | 0.11364 | 0.28636 | 0.33182 | 0.42727 | 0.65909 | 0.65909 | 0.65909
| Moisture Removal |  | (L/h) | 1.05 | 1.5 | 2.1 | 3 | 3.6 | 5.1 | 5.5
| Noise level(Hi/Mi/Lo) |  | dB(A) | 41/38/32 | 41/38/32 | 45/42/36 | 48/45/39 | 50/47/41 | 50/47/41 | 50/47/41
| Extemal static pressure |  | Pa | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unit dimension (W*H*D) |  | mm | 580x255x580 | 580x255x580 | 835x240x835 | 835x240x835 | 835x280x835 | 835x280x835 | 835x280x835
| Packing (W*H*D) |  | mm | 680x320x680 | 680x320x680 | 900x320x900 | 900x320x900 | 900x360x900 | 900x360x900 | 900x360x900
| Net weight |  | Kg | 20 | 20 | 27 | 27 | 30 | 30 | 30
| Gross weight |  | Kg | 25 | 25 | 34 | 34 | 37 | 37 | 37
Panel | Unit dimension (W*H*D) |  | mm | 650×650×30 | 650×650×30 | 950×950×55 | 950×950×55 | 950×950×55 | 950×950×55 | 950×950×55
| Packing (W*H*D) |  | mm | 740×740×145 | 740×740×145 | 1000×1000×100 | 1000×1000×100 | 1000×1000×100 | 1000×1000×100 | 1000×1000×100
| Net weight |  | Kg | 3 | 3 | 5 | 5 | 5 | 5 | 5
| Gross weight |  | Kg | 5 | 5 | 7 | 7 | 7 | 7 | 7
Outdoor unit | Outdoor fan motor | Model |  | YDK30-6A | YDK65-6B | YDK85-6-50 | YDK150-6C-420 | YDK150-6C-420 | YDK68-6-359 | YDK68-6-359
|  | Brand |  | AUX | AUX | AUX | WEITELI | WEITELI | WEITELI | WEITELI
|  | Output Power | W | 30 | 65 | 85 | 150 | 150 | 68 | 68
|  | Capacitor | uF | 2.5 | 4 | 4 | 6 | 6 | 3 | 3
|  | Speed | r/min | 770 | 870 | 900 | 800 | 800 | 860 | 860
| Outdoor coil | a.Number of row |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | b.Tube pitch(a)x row pitch(b) | mm | 20.5×12.7 | 22×19.05 | 22×19.05 | 22/19.05 | 22/19.05 | 22/19.05 | 22/19.05
|  | c.Fin spacing | mm | 1.6 | 1.6 | 1.5 | 1.6 | 1.6 | 1.6 | 1.6
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved
|  | f.Coil length x height x width | mm | 850×492×25.4 | 760×484×38.1 | 776×660×38.1 | 889×814×38.1 | 889×814×38.1 | 750×1188×38.1 | 750×1188×38.1
|  | g.Number of U-Tube |  | 12 | 24 | 30 | 36 | 36 | 54 | 54
|  | h. Number of circuits |  | 4 | 4 | 5 | 6 | 6 | 9 | 9
|  | i.Heat exchanging area | m2 | 11.79 | 17.6575 | 23.71 | 30.6625 | 30.6625 | 38.8502 | 38.8502
| Noise level |  | dB(A) | 53 | 55 | 60 | 60 | 62 | 62 | 62
| Unit dimension (W*H*D) |  | mm | 760x540x260 | 800x590x300 | 800x690x300 | 903x857x354 | 903x857x354 | 945x1255x340 | 945x1255x340
| Packing (W*H*D) |  | mm | 880x610x350 | 930x660x410 | 930x660x410 | 1030x980x410 | 1030x980x410 | 1090x1370x430 | 1090x1370x430
| Net weight |  | Kg | 38 | 45 | 56 | 86 | 88 | 97 | 105
| Gross weight |  | Kg | 41 | 49 | 60 | 94 | 96 | 110 | 119
| Refrigerant type |  |  | R410A | R410A | R410A | R410A | R410A | R410A | R410A
| Refrigerant charge |  | g | 1165 | 1360 | 2360 | 2830 | 2310 | 2890 | 3310
| Design pressure |  | MPa | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15
Refrigerant pipe |  | Liquid side | mm | 6.35 | 6.35 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
|  | Gas side | mm | 12.7 | 12.7 | 15.88 | 15.88 | 19.05 | 19.05 | 19.05
|  | Max. refrigerant pipe length | m | 25 | 25 | 30 | 30 | 50 | 50 | 50
|  | Max. difference in level | m | 10 | 10 | 15 | 20 | 20 | 20 | 20
Operation temperature range |  |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient temperature range(Cooling/Heating) |  |  | ℃ | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24
Application area |  |  | m2 | 15~35 | 20~50 | 30~70 | 40~100 | 50~120 | 60~140 | 80~180
Qty’per 20’& 40’&40HQ(only for reference) |  |  | Set | 61/128/154 | 53/111/132 | 38/81/95 | 32/67/78 | 30/64/74 | 23/49/56 | 23/49/56

## T1 50Hz R410A CE (hidden)
Return |  | Model |  | ALCe-H12A4/R1-C3 | ALCe-H18A4/R1-C3 | ALCe-H24B4/R1-C3 | ALCe-H36A5/R1-C3 | ALCe-H42A5/R1-C3 | ALCe-H48A5/R1-C3 | ALCe-H60A5/R1-C3
Power supply |  |  | Ph-V-Hz | 1Ph / 220-240V/50HZ | 1Ph / 220-240V/50HZ | 1Ph / 220-240V/50HZ | 3Ph / 380-415V/50HZ | 3Ph / 380-415V/50HZ | 3Ph / 380-415V/50HZ | 3Ph / 380-415V/50HZ
Cooling |  | Capacity | W | 3600 | 5300 | 7200 | 10600 | 12000 | 14000 | 17600
|  |  | BTU | 12000 | 18000 | 24000 | 36000 | 42000 | 48000 | 60000
|  | Input | W | 1300 | 1940 | 2700 | 3850 | 4600 | 4870 | 6280
|  | Rated current | A | 6 | 8.91 | 12.5 | 6.9 | 8.42 | 8.88 | 11.46
|  | EER |  | 2.7692 | 2.732 | 2.6667 | 2.7532 | 2.6087 | 2.8747 | 2.8025
Heating |  | Capacity | W | 3900 | 5800 | 8080 | 11700 | 14000 | 15500 | 18500
|  |  | BTU | 13200 | 19800 | 26400 | 39600 | 46200 | 52800 | 66000
|  | Input | W | 1220 | 1900 | 2500 | 3500 | 4700 | 5130 | 5970
|  | Rated current | A | 5.72 | 8.73 | 11.59 | 6.28 | 8.56 | 9.33 | 10.83
|  | COP |  | 3.1967 | 3.0526 | 3.232 | 3.3429 | 2.9787 | 3.0214 | 3.0988
Max. input consumption |  |  | W | 1750 | 2650 | 3650 | 4570 | 5800 | 6100 | 7800
Max. current |  |  | A | 7.9545 | 12.0455 | 16.5909 | 12.0263 | 15.2632 | 16.0526 | 20.5263
Compressor |  | Model |  | PA150X2C-4FT | PA215X2CS-4KU1 | PA290X3CS-4MUI | C-SBP130H38A | C-SBP160H38A | C-SBP170H38A | JT170G-P8Y1
|  | Type |  | ROTARY | ROTARY | ROTARY | SCROLL | SCROLL | SCROLL | SCROLL
|  | Brand |  | TOSHIBA | TOSHIBA | TOSHIBA | SANYO | SANYO | SANYO | DAKIN
|  | Capacity | W | 3670 | 5340 | 7180 | 10900 | 13200 | 14100 | 15900
|  | Input | W | 1245 | 1830 | 2430 | 3750 | 4600 | 4750 | 4500
|  | Rated current(RLA) | A | 5.75 | 8.55 | 11.4 | 6.8 | 8.61 | 8.68 | 8.9
|  | Locked rotor Amp(LRA) | A | 29.9 | 36.8 | 61 | 66 | 73 | 63 | 59.4
|  | Thermal protector |  | UP3RE0596-T56 | UP3SE0391-T39 | UP14SE5145 | UP18 | UP18 | UP18 | UP18WA162-46G
|  | Capacitor | uF | 35 | 50 | 50 | / | / | / | /
|  | Refrigerant oil | ml | 480 | 750 | 950 | 1700 | 1700 | 1700 | 1500
Indoor unit | Indoor fan motor | Model |  | YSK15-6 | YSK35-4 | YSK60-4 | YSK75-4 | YSK125-4 | YSK125-4 | YSK125-4
|  | Brand |  | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO
|  | Output Power | W | 15 | 35 | 60 | 75 | 125 | 125 | 125
|  | Capacitor | uF | 1.5 | 3 | 3 | 4 | 5 | 5 | 5
|  | Speed (Hi/Mi/Lo) | r/min | 820/650/420 | 1050/850/750 | 910/780/690 | 1250/1180/982 | 1370/1180/1080 | 1370/1180/1080 | 1370/1180/1080
| Indoor coil | a.Number of row |  | 2 | 3 | 3 | 3 | 3 | 3 | 3
|  | b.Tube pitch(a)x row pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
|  | c.Fin spacing | mm | 1.4 | 1.4 | 1.6 | 1.5 | 1.5 | 1.5 | 1.5
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
|  | f.Coil length x height x width | mm | 570×266.5×25.4 | 570×266.5×38.1 | 950×266.5×38.1 | 950×266.5×38.1 | 1333×266.5×38.1 | 1333×266.5×38.1 | 1333×266.5×38.1
|  | g.Number of U-Tube |  | 13 | 19 | 18 | 18 | 18 | 18 | 18
|  | h. Number of circuits |  | 2 | 3 | 6 | 6 | 6 | 6 | 6
|  | i.Heat exchanging area | m2 | 4.9045 | 7.1681 | 10 | 10.6172 | 14.8641 | 14.8641 | 14.8641
| Indoor air flow (Hi/Mi/Lo) |  | m3/h | 650/520/455 | 920/736/644 | 1200/960/840 | 1500/1200/1050 | 1800/1440/1260 | 1800/1440/1260 | 1800/1440/1260
| Rated input Power(cooling/heating) |  | W | 38 | 85 | 125 | 156 | 192 | 192 | 192
| Rated current (cooling/heating) |  | A | 0.17273 | 0.38636 | 0.56818 | 0.70909 | 0.87273 | 0.87273 | 0.87273
| Moisture Removal |  | (L/h) | 1.05 | 1.5 | 2.1 | 3 | 3.6 | 5.1 | 5.5
| Noise level(Hi/Mi/Lo) |  | dB(A) | 39/36/30 | 43/40/34 | 46/43/37 | 50/47/41 | 51/48/42 | 51/48/42 | 51/48/42
| Extemal static pressure |  | Pa | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Unit dimension (W*H*D) |  | mm | 950x673x243 | 950x673x243 | 1333x673x243 | 1333x673x243 | 1715x673x243 | 1715x673x243 | 1715x673x243
| Packing (W*H*D) |  | mm | 995x740x320 | 995x740x320 | 1375x740x320 | 1375x740x320 | 1760x740x320 | 1760x740x320 | 1760x740x320
| Net weight |  | Kg | 24 | 25 | 33 | 33 | 41 | 41 | 41
| Gross weight |  | Kg | 28 | 29 | 38 | 38 | 47 | 47 | 47
Outdoor unit | Outdoor fan motor | Model |  | YDK30-6A | YDK65-6B | YDK85-6-50 | YDK150-6C-420 | YDK150-6C-420 | YDK68-6-359 | YDK68-6-359
|  | Brand |  | AUX | AUX | AUX | WEITELI | WEITELI | WEITELI | WEITELI
|  | Output Power | W | 30 | 65 | 85 | 150 | 150 | 68 | 68
|  | Capacitor | uF | 2.5 | 4 | 4 | 6 | 6 | 3 | 3
|  | Speed | r/min | 770 | 870 | 900 | 800 | 800 | 860 | 860
| Outdoor coil | a.Number of row |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  | b.Tube pitch(a)x row pitch(b) | mm | 20.5×12.7 | 22×19.05 | 22×19.05 | 22/19.05 | 22/19.05 | 22/19.05 | 22/19.05
|  | c.Fin spacing | mm | 1.6 | 1.6 | 1.5 | 1.6 | 1.6 | 1.6 | 1.6
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved
|  | f.Coil length x height x width | mm | 850×492×25.4 | 760×484×38.1 | 776×660×38.1 | 889×814×38.1 | 889×814×38.1 | 750×1188×38.1 | 750×1188×38.1
|  | g.Number of U-Tube |  | 12 | 24 | 30 | 36 | 36 | 54 | 54
|  | h. Number of circuits |  | 4 | 4 | 5 | 6 | 6 | 9 | 9
|  | i.Heat exchanging area | m2 | 11.79 | 17.6575 | 23.71 | 30.6625 | 30.6625 | 38.8502 | 38.8502
| Noise level |  | dB(A) | 53 | 55 | 60 | 60 | 62 | 62 | 62
| Unit dimension (W*H*D) |  | mm | 760x540x260 | 800x590x300 | 800x690x300 | 903x857x354 | 903x857x354 | 945x1255x340 | 945x1255x340
| Packing (W*H*D) |  | mm | 880x610x350 | 930x660x410 | 930x660x410 | 1030x980x410 | 1030x980x410 | 1090x1370x430 | 1090x1370x430
| Net weight |  | Kg | 38 | 45 | 56 | 86 | 88 | 97 | 105
| Gross weight |  | Kg | 41 | 49 | 60 | 94 | 96 | 110 | 119
| Refrigerant type |  |  | R410A | R410A | R410A | R410A | R410A | R410A | R410A
| Refrigerant charge |  | g | 1165 | 1360 | 2360 | 2830 | 2310 | 2890 | 3310
| Design pressure |  | MPa | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15
Refrigerant pipe |  | Liquid side | mm | 6.35 | 6.35 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
|  | Gas side | mm | 12.7 | 12.7 | 15.88 | 15.88 | 19.05 | 19.05 | 19.05
|  | Max. refrigerant pipe length | m | 25 | 25 | 30 | 30 | 50 | 50 | 50
|  | Max. difference in level | m | 10 | 10 | 15 | 20 | 20 | 20 | 20
Operation temperature range |  |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient temperature range(Cooling/Heating) |  |  | ℃ | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24
Application area |  |  | m2 | 15~35 | 20~50 | 30~70 | 40~100 | 50~120 | 60~140 | 80~180
Qty’per 20’& 40’&40HQ(only for reference) |  |  | Set | 60/126/151 | 52/109/130 | 40/85/100 | 33/71/82 | 29/62/72 | 22/48/54 | 22/48/54

## T1 50Hz R410A DU (hidden)
Return |  | Model |  | ALDu-H12A4/R1-S3
Power supply |  |  | Ph-V-Hz | 1Ph / 220-240V/50HZ
Cooling |  | Capacity | W | 3600
|  |  | BTU | 12000
|  | Input | W | 1300
|  | Rated current | A | 6
|  | EER |  | 2.7692
Heating |  | Capacity | W | 3900
|  |  | BTU | 13200
|  | Input | W | 1220
|  | Rated current | A | 5.72
|  | COP |  | 3.1967
Max. input consumption |  |  | W | 1750
Max. current |  |  | A | 7.9545
Compressor |  | Model |  | PA150X2C-4FT
|  | Type |  | ROTARY
|  | Brand |  | TOSHIBA
|  | Capacity | W | 3670
|  | Input | W | 1245
|  | Rated current(RLA) | A | 5.75
|  | Locked rotor Amp(LRA) | A | 29.9
|  | Thermal protector |  | UP3RE0596-T56
|  | Capacitor | uF | 35
|  | Refrigerant oil | ml | 480
Indoor unit | Indoor fan motor | Model |  | YSK22-4
|  | Brand |  | HUATE
|  | Output Power | W | 22
|  | Capacitor | uF | 1.5
|  | Speed (Hi/Mi/Lo) | r/min | 750/680/650
| Indoor coil | a.Number of row |  | 2
|  | b.Tube pitch(a)x row pitch(b) | mm | 20.5×12.7
|  | c.Fin spacing | mm | 1.4
|  | d.Fin material |  | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7， Inner grooved
|  | f.Coil length x height x width | mm | 685×205×25.4
|  | g.Number of U-Tube |  | 10
|  | h. Number of circuits |  | 3
|  | i.Heat exchanging area | m2 | 4.53
| Indoor air flow (Hi/Mi/Lo) |  | m3/h | 630/504/441
| Rated input Power(cooling/heating) |  | W | 60
| Rated current (cooling/heating) |  | A | 0.27273
| Moisture Removal |  | (L/h) | 1.05
| Noise level(Hi/Mi/Lo) |  | dB(A) | 38/35/29
| Extemal static pressure |  | Pa | 12/30
| Unit dimension (W*H*D) |  | mm | 880×240×528
| Packing (W*H*D) |  | mm | 980×280×620
| Net weight |  | Kg | 21.5
| Gross weight |  | Kg | 25
Outdoor unit | Outdoor fan motor | Model |  | YDK30-6A
|  | Brand |  | AUX
|  | Output Power | W | 30
|  | Capacitor | uF | 2.5
|  | Speed | r/min | 770
| Outdoor coil | a.Number of row |  | 2
|  | b.Tube pitch(a)x row pitch(b) | mm | 20.5×12.7
|  | c.Fin spacing | mm | 1.6
|  | d.Fin material |  | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7， Inner grooved
|  | f.Coil length x height x width | mm | 850×492×25.4
|  | g.Number of U-Tube |  | 12
|  | h. Number of circuits |  | 2
|  | i.Heat exchanging area | m2 | 11.79
| Noise level |  | dB(A) | 53
| Unit dimension (W*H*D) |  | mm | 760x540x260
| Packing (W*H*D) |  | mm | 880x610x350
| Net weight |  | Kg | 38
| Gross weight |  | Kg | 41
| Refrigerant type |  |  | R410A
| Refrigerant charge |  | g | 1165
| Design pressure |  | MPa | 4.15
Refrigerant pipe |  | Liquid side | mm | 6.35
|  | Gas side | mm | 12.7
|  | Max. refrigerant pipe length | m | 25
|  | Max. difference in level | m | 10
Operation temperature range |  |  | ℃ | 16~32
Ambient temperature range(Cooling/Heating) |  |  | ℃ | -15~49/-15~24
Application area |  |  | m2 | 15~35
Qty’per 20’& 40’&40HQ(only for reference) |  |  | Set | 71/149/180

## T1 50Hz R410A HI (hidden)
Return |  | Model |  | ALHi-H18A4/R1-C5 | ALHi-H24B4/R1-C5 | ALHi-H36A5/R1-C5 | ALHi-H42A5/R1-C5 | ALHi-H48A5/R1-C5 | ALHi-H60A5/R1-C5
Power supply |  |  | Ph-V-Hz | 1Ph / 220-240V/50HZ | 1Ph / 220-240V/50HZ | 3Ph / 380-415V/50HZ | 3Ph / 380-415V/50HZ | 3Ph / 380-415V/50HZ | 3Ph / 380-415V/50HZ
Cooling |  | Capacity | W | 5300 | 7200 | 10600 | 12000 | 14000 | 17600
|  |  | BTU | 18000 | 24000 | 36000 | 42000 | 48000 | 60000
|  | Input | W | 1940 | 2700 | 3850 | 4600 | 4870 | 6280
|  | Rated current | A | 8.91 | 12.5 | 6.9 | 8.42 | 8.88 | 11.46
|  | EER |  | 2.732 | 2.6667 | 2.7532 | 2.6087 | 2.8747 | 2.8025
Heating |  | Capacity | W | 5800 | 8080 | 11700 | 14000 | 15500 | 18500
|  |  | BTU | 19800 | 26400 | 39600 | 46200 | 52800 | 66000
|  | Input | W | 1900 | 2500 | 3500 | 4700 | 5130 | 5970
|  | Rated current | A | 8.73 | 11.59 | 6.28 | 8.56 | 9.33 | 10.83
|  | COP |  | 3.0526 | 3.232 | 3.3429 | 2.9787 | 3.0214 | 3.0988
Max. input consumption |  |  | W | 2700 | 3750 | 4570 | 5800 | 5950 | 7800
Max. current |  |  | A | 12.2727 | 17.0455 | 12.0263 | 15.2632 | 15.6579 | 20.5263
Compressor |  | Model |  | PA215X2CS-4KU1 | PA290X3CS-4MUI | C-SBP130H38A | C-SBP160H38A | C-SBP170H38A | JT170G-P8Y1
|  | Type |  | ROTARY | ROTARY | SCROLL | SCROLL | SCROLL | SCROLL
|  | Brand |  | TOSHIBA | TOSHIBA | SANYO | SANYO | SANYO | DAKIN
|  | Capacity | W | 5340 | 7180 | 10900 | 13200 | 14100 | 15900
|  | Input | W | 1830 | 2430 | 3750 | 4600 | 4750 | 4500
|  | Rated current(RLA) | A | 8.55 | 11.4 | 6.8 | 8.61 | 8.68 | 8.9
|  | Locked rotor Amp(LRA) | A | 36.8 | 61 | 66 | 73 | 63 | 59.4
|  | Thermal protector |  | UP3SE0391-T39 | UP14SE5145 | UP18 | UP18 | UP18 | UP18WA162-46G
|  | Capacitor | uF | 50 | 50 | / | / | / | /
|  | Refrigerant oil | ml | 750 | 950 | 1700 | 1700 | 1700 | 1500
Indoor unit | Indoor fan motor | Model |  | YSK100-4 | YSK160-4 | YSK180-4 | YSK180-4 | YSK180-4 | YSK180-4
|  | Brand |  | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO
|  | Output Power | W | 100 | 160 | 180 | 180 | 180 | 180
|  | Capacitor | uF | 3 | 2.5 | 5 | 6 | 6 | 6
|  | Speed (Hi/Mi/Lo) | r/min | 960/860/840 | 1050/1000/910 | 1050/1000/910 | 1100/990/920 | 1100/990/920 | 1100/990/920
| Indoor coil | a.Number of row |  | 2 | 3 | 3 | 3 | 3 | 3
|  | b.Tube pitch(a)x row pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
|  | c.Fin spacing | mm | 1.5 | 1.6 | 1.5 | 1.6 | 1.6 | 1.6
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
|  | f.Coil length x height x width | mm | 625×369×25.4 | 625×369×38.1 | 625×369×38.1 | 985×369×38.1 | 985×369×38.1 | 985×369×38.1
|  | g.Number of U-Tube |  | 18 | 27 | 27 | 27 | 27 | 27
|  | h. Number of circuits |  | 3 | 5 | 5 | 9 | 9 | 9
|  | i.Heat exchanging area | m2 | 6.9626 | 9.8407 | 10.444 | 15.5587 | 15.5587 | 15.5587
| Indoor air flow (Hi/Mi/Lo) |  | m3/h | 950/760/665 | 1200/960/840 | 1500/1200/1050 | 2000/1600/1400 | 2000/1600/1400 | 2000/1600/1400
| Rated input Power(cooling/heating) |  | W | 149 | 214 | 260 | 316 | 316 | 316
| Rated current (cooling/heating) |  | A | 0.67727 | 0.97273 | 1.1818 | 1.4364 | 1.4364 | 1.4364
| Moisture Removal |  | (L/h) | 1.5 | 2.1 | 3 | 3.6 | 5.1 | 5.5
| Noise level(Hi/Mi/Lo) |  | dB(A) | 44/41/35 | 47/44/38 | 50/47/41 | 53/50/44 | 53/50/44 | 53/50/44
| Extemal static pressure |  | Pa | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80
| Unit dimension (W*H*D) |  | mm | 890×290×785 | 890×290×785 | 890×290×785 | 1250×290×785 | 1250×290×785 | 1250×290×785
| Packing (W*H*D) |  | mm | 1100×360×870 | 1100×360×870 | 1100×360×870 | 1460×360×870 | 1460×360×870 | 1460×360×870
| Net weight |  | Kg | 34 | 36 | 36 | 41 | 41 | 41
| Gross weight |  | Kg | 40 | 42 | 42 | 47 | 47 | 47
Outdoor unit | Outdoor fan motor | Model |  | YDK65-6B | YDK85-6-50 | YDK150-6C-420 | YDK150-6C-420 | YDK68-6-359 | YDK68-6-359
|  | Brand |  | AUX | AUX | WEITELI | WEITELI | WEITELI | WEITELI
|  | Output Power | W | 65 | 85 | 150 | 150 | 68 | 68
|  | Capacitor | uF | 4 | 4 | 6 | 6 | 3 | 3
|  | Speed | r/min | 870 | 900 | 800 | 800 | 860 | 860
| Outdoor coil | a.Number of row |  | 2 | 2 | 2 | 2 | 2 | 2
|  | b.Tube pitch(a)x row pitch(b) | mm | 22×19.05 | 22×19.05 | 22/19.05 | 22/19.05 | 22/19.05 | 22/19.05
|  | c.Fin spacing | mm | 1.6 | 1.5 | 1.6 | 1.6 | 1.6 | 1.6
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved | φ7.94， Inner grooved
|  | f.Coil length x height x width | mm | 760×484×38.1 | 776×660×38.1 | 889×814×38.1 | 889×814×38.1 | 750×1188×38.1 | 750×1188×38.1
|  | g.Number of U-Tube |  | 24 | 30 | 36 | 36 | 54 | 54
|  | h. Number of circuits |  | 4 | 5 | 6 | 6 | 9 | 9
|  | i.Heat exchanging area | m2 | 17.6575 | 23.71 | 30.6625 | 30.6625 | 38.8502 | 38.8502
| Noise level |  | dB(A) | 55 | 60 | 60 | 62 | 62 | 62
| Unit dimension (W*H*D) |  | mm | 800x590x300 | 800x690x300 | 903x857x354 | 903x857x354 | 945x1255x340 | 945x1255x340
| Packing (W*H*D) |  | mm | 930x660x410 | 930x660x410 | 1030x980x410 | 1030x980x410 | 1090x1370x430 | 1090x1370x430
| Net weight |  | Kg | 45 | 56 | 86 | 88 | 97 | 105
| Gross weight |  | Kg | 49 | 60 | 94 | 96 | 110 | 119
| Refrigerant type |  |  | R410A | R410A | R410A | R410A | R410A | R410A
| Refrigerant charge |  | g | 1360 | 2360 | 2830 | 2310 | 2890 | 3310
| Design pressure |  | MPa | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15
Refrigerant pipe |  | Liquid side | mm | 6.35 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
|  | Gas side | mm | 12.7 | 15.88 | 15.88 | 19.05 | 19.05 | 19.05
|  | Max. refrigerant pipe length | m | 25 | 30 | 30 | 50 | 50 | 50
|  | Max. difference in level | m | 10 | 15 | 20 | 20 | 20 | 20
Operation temperature range |  |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient temperature range(Cooling/Heating) |  |  | ℃ | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24 | -15~49/-15~24
Application area |  |  | m2 | 20~50 | 30~70 | 40~100 | 50~120 | 60~140 | 80~180
Qty’per 20’& 40’&40HQ(only for reference) |  |  | Set | 42/88/103 | 39/83/96 | 32/69/79 | 28/59/67 | 21/46/51 | 21/46/51

## T3 60Hz R22 CA (hidden)
Return |  | Model |  | 型号 |  |  |  | ALTCa-H18A2/C5 | ALTCa-H24B2/C5 | ALTCa-H30A2/C5 | ALTCa-H36A2/C5 | ALTCa-H48A2/C5 | ALTCa-H60A2/C5
Power supply |  |  | Ph-V-Hz | 电源 |  |  | Ph-V-Hz | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ
Cooling |  | Capacity | W | 制冷 |  | 制冷量 | W | 5100 | 7200 | 8500 | 10000 | 14000 | 17000
|  |  | BTU |  |  |  | BTU | 18000 | 24000 | 30000 | 36000 | 48000 | 60000
|  | Input | W |  |  | 输入功率 | W | 1900 | 2720 | 3250 | 3850 | 5540 | 6810
|  | Rated current | A |  |  | 额定电流 | A | 8.73 | 12.83 | 15 | 6.9 | 10.1 | 12.43
|  | EER |  |  |  | EER |  | 2.6842 | 2.6471 | 2.6154 | 2.5974 | 2.5271 | 2.4963
Heating |  | Capacity | W | 制热 |  | 制热量 | W | 5600 | 7900 | 9300 | 11000 | 15000 | 17500
|  |  | BTU |  |  |  | BTU | 19800 | 26400 | 33000 | 39600 | 52800 | 66000
|  | Input | W |  |  | 输入功率 | W | 1750 | 2500 | 3130 | 3680 | 5500 | 6680
|  | Rated current | A |  |  | 额定电流 | A | 8.11 | 12 | 14.3 | 6.6 | 10 | 12.13
|  | COP |  |  |  | COP |  | 3.2 | 3.16 | 2.9712 | 2.9891 | 2.7273 | 2.6198
Max. input consumption |  |  | W | 最大输入功率 |  |  | W | 2650 | 3200 | 4100 | 4570 | 6100 | 7800
Max. current |  |  | A | 最大电流 |  |  | A | 12.0455 | 14.5455 | 18.6364 | 20.7727 | 27.7273 | 35.4545
Compressor |  | Model |  | 压缩机 |  | 型号 |  | SHZ83LC4-E | SHW73TC4-E | PH370X3CJ-3MTS | SHV73YC1-E | C-SBR145H16P | C-SBR165H16P
|  | Type |  |  |  | 类型 |  | ROTARY | ROTARY | ROTARY | ROTARY | SCROLL | SCROLL
|  | Brand |  |  |  | 品牌 |  | HITACHI | HITACHI | TOSHIBA | HITACHI | SANYO | SANYO
|  | Capacity | W |  |  | 压缩机能力 | W | 6030 | 7330 | 7920 | 8520 | 14200 | 16700
|  | Input | W |  |  | 输入功率 | W | 2025 | 2445 | 2610 | 2940 | 4550 | 5300
|  | Rated current(RLA) | A |  |  | 额定电流 | A | 9.4 | 12 | 12.65 | 14.5 | 22.6 | 27.1
|  | Locked rotor Amp(LRA) | A |  |  | 锁定转子电流 | A | 42 | 65 | / | 75 | / | /
|  | Thermal protector |  |  |  | Thermal protector （热力保护器） |  | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 150℃ | Inside Eclass 160℃
|  | Capacitor | uF |  |  | 电容 | uF | 50 | 60 | 55 | 60 | 70 | 80
|  | Refrigerant oil | ml |  |  | 压缩机油 | ml | 600 | 600 | 750 | 875 | 1400 | 1400
Indoor unit | Indoor fan motor | Model |  | 内机 | 内机风机 | 型号 |  | YDK25-6-50 Q | YDK30-6 Q | YDK35-6 Q | YDK45-6 Q | YDK80-6-50 Q | YDK80-6-50 Q
|  | Brand |  |  |  | 品牌 |  | HUATE | HUATE | HUATE | HUATE | KANGBAO | KANGBAO
|  | Output Power | W |  |  | 输出功率 | W | 25 | 30 | 35 | 45 | 80 | 80
|  | Capacitor | uF |  |  | 电容 | uF | 2.5 | 3 | 4 | 4 | 6 | 6
|  | Speed (Hi/Mi/Lo) | r/min |  |  | 转速（高/中/低） | r/min | 930/750/650 | 500/400/320 | 570/480/400 | 650/520/450 | 685/540/450 | 685/540/450
| Indoor coil | a.Number of row |  |  | 内机蒸发器 | a.排数 |  | 2 | 2 | 2 | 2 | 2 | 2
|  | b.Tube pitch(a)x row pitch(b) | mm |  |  | b.管心距(a)x 行距(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
|  | c.Fin spacing | mm |  |  | c.翅片间距 | mm | 1.5 | 1.6 | 1.4 | 1.4 | 1.4 | 1.4
|  | d.Fin material |  |  |  | d.翅片材料 |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm |  |  | e.管外径和材料 | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
|  | f.Coil length x height x width | mm |  |  | f.蒸发器 长 x 高 x 宽 | mm | 1115×205×25.4 | 2142×205×25.4 | 2142×205×25.5 | 2142×205×25.4 | 2142×246×25.6 | 2142×246×25.7
|  | g.Number of U-Tube |  |  |  | g.U型管数量 |  | 8 | 8 | 9 | 9 | 11 | 11
|  | h. Number of circuits |  |  |  | h.分路数 |  | 4 | 8 | 9 | 9 | 11 | 11
|  | i.Heat exchanging area | m2 |  |  | i.换热面积 |  | 4.846 | 10.025 | 10.025 | 12.7597 | 15.5952 | 15.5952
| Indoor air flow (Hi/Mi/Lo) |  | m3/h |  | 内机风量(高/中/低) |  | m3/h | 850/680/595 | 1100/880/770 | 1500/1200/1050 | 1500/1200/1050 | 1700/1360/1190 | 1700/1360/1190
| Rated input Power(cooling/heating) |  | W |  | 额定输入功率(cooling/heating) |  | W | 63 | 73 | 82 | 94 | 145 | 145
| Rated current (cooling/heating) |  | A |  | 输入电流 (cooling/heating) |  | A | 0.28636 | 0.33182 | 0.37273 | 0.42727 | 0.65909 | 0.65909
| Moisture Removal |  | (L/h) |  | 除湿量 |  | (L/h) | 1.5 | 2.1 | 2.6 | 3 | 5.1 | 5.5
| Noise level(Hi/Mi/Lo) |  | dB(A) |  | 噪音等级(高/中/低) |  | dB(A) | 41/38/32 | 45/42/36 | 48/45/39 | 48/45/39 | 50/47/41 | 50/47/41
| Extemal static pressure |  | Pa |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Unit dimension (W*H*D) |  | mm |  | 机组尺寸 (宽*高*深) |  | mm | 580x255x580 | 835x240x835 | 835x240x835 | 835x240x835 | 835x280x835 | 835x280x835
| Packing (W*H*D) |  | mm |  | 包装尺寸 (宽*高*深) |  | mm | 680x320x680 | 900x320x900 | 900x320x900 | 900x320x900 | 900x360x900 | 900x360x900
| Net weight |  | Kg |  | 净重 |  | Kg | 20 | 27 | 27 | 27 | 30 | 30
| Gross weight |  | Kg |  | 毛重 |  | Kg | 25 | 34 | 34 | 34 | 37 | 37
Panel | Unit dimension (W*H*D) |  | mm |  |  |  |  | 650×650×30 | 950×950×55 | 950×950×55 | 950×950×55 | 950×950×55 | 950×950×55
| Packing (W*H*D) |  | mm |  |  |  |  | 740×740×145 | 1000×1000×100 | 1000×1000×100 | 1000×1000×100 | 1000×1000×100 | 1000×1000×100
| Net weight |  | Kg |  |  |  |  | 3 | 5 | 5 | 5 | 5 | 5
| Gross weight |  | Kg |  |  |  |  | 5 | 7 | 7 | 7 | 7 | 7
Outdoor unit | Outdoor fan motor | Model |  | 外机 | 外风机 | 型号 |  | YDK65-6C-60 | YDK68-6B-60 | YDK68-6B-60 | YDK120-6C-60 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3
|  | Brand |  |  |  | 品牌 |  | AUX | AUX | AUX | AUX | WEITELI | WEITELI
|  | Output Power | W |  |  | 输出功率 | W | 65 | 68 | 68 | 120 | 70 | 70
|  | Capacitor | uF |  |  | 电容 | uF | 4 | 4 | 4 | 6 | 3 | 3
|  | Speed | r/min |  |  | 转速 | r/min | 870 | 900 | 900 | 800 | 860 | 860
| Outdoor coil | a.Number of row |  |  | 外机冷凝器 | a.排数 |  | 2 | 2 | 2 | 2 | 2 | 2
|  | b.Tube pitch(a)x row pitch(b) | mm |  |  | b.管心距(a)x 行距(b) | mm | 22/19.05 | 25.4×22 | 25.4×22 | 25.4×22 | 22/19.05 | 25.4×22
|  | c.Fin spacing | mm |  |  | c.翅片间距 | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
|  | d.Fin material |  |  |  | d.翅片材料 |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm |  |  | e.管外径和材料 | mm | φ7.94， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ7.94， Inner grooved | φ9.52， Inner grooved
|  | f.Coil length x height x width | mm |  |  | f. 冷凝器 长 x 高 x 宽 | mm | 760×484×38.1 | 733×660.4×44 | 733×660.4×44 | 844×762×44 | 750×1188×38.1 | 750×1219.5×44
|  | g.Number of U-Tube |  |  |  | g.U型管数量 |  | 24 | 26 | 26 | 30 | 54 | 48
|  | h. Number of circuits |  |  |  | h.分路数 |  | 4 | 4 | 4 | 4 | 9 | 8
|  | i.Heat exchanging area | m2 |  |  | i.换热面积 |  | 17.6575 | 23.9982 | 23.9982 | 31.88 | 38.8502 | 45.3033
| Noise level |  | dB(A) |  | 噪音等级 |  | dB(A) | 55 | 60 | 60 | 60 | 62 | 62
| Unit dimension (W*H*D) |  | mm |  | 机组尺寸 (宽*高*深) |  | mm | 800x590x300 | 800x690x300 | 800x690x300 | 900×790×320 | 945x1255x340 | 945x1255x340
| Packing (W*H*D) |  | mm |  | 包装尺寸 (宽*高*深) |  | mm | 930x660x410 | 930x760x410 | 930x760x410 | 1030×850×430 | 1090x1370x430 | 1090x1370x430
| Net weight |  | Kg |  | 净重 |  | Kg | 45 | 56 | 60 | 64 | 97 | 105
| Gross weight |  | Kg |  | 毛重 |  | Kg | 49 | 60 | 64 | 69 | 110 | 119
| Refrigerant type |  |  |  | 冷媒类型 |  |  | R22 | R22 | R22 | R22 | R22 | R22
| Refrigerant charge |  | g |  | 冷媒充注量 |  | g | 1360 | 1732 | 2070 | 2630 | 2630 | 3360
| Design pressure |  | MPa |  | 设计压力 |  | MPa | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
Refrigerant pipe |  | Liquid side | mm | 冷媒管 |  | 液管 | mm | 6.35 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
|  | Gas side | mm |  |  | 气管 | mm | 12.7 | 15.88 | 15.88 | 15.88 | 19.05 | 19.05
|  | Max. refrigerant pipe length | m |  |  | 最大管长 | m | 25 | 30 | 30 | 30 | 50 | 50
|  | Max. difference in level | m |  |  | 最大落差 | m | 10 | 15 | 15 | 15 | 20 | 20
Operation temperature range |  |  | ℃ | 可运行温度范围 |  |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient temperature range(Cooling/Heating) |  |  | ℃ | 环境温度范围(制冷/制热) |  |  | ℃ | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24
Application area |  |  | m2 | 适用面积 |  |  | m2 | 20~50 | 30~70 | 35~85 | 40~100 | 60~140 | 80~180
Qty’per 20’& 40’&40HQ(only for reference) |  |  | Set | 装柜量r 20’& 40’&40HQ(仅供参考) |  |  | Set | 53/111/132 | 38/81/95 | 38/81/95 | 36/74/90 | 23/49/56 | 23/49/56

## T3 60Hz R22 CE (hidden)
Return |  | Model |  | ALTCe-H18A2/C3 | ALTCe-H24B2/C3 | ALTCe-H30A2/C3 | ALTCe-H36A2/C3 | ALTCe-H48A2/C3 | ALTCe-H60A2/C3
Power supply |  |  | Ph-V-Hz | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ
Cooling |  | Capacity | W | 5100 | 7200 | 8500 | 10000 | 14000 | 17000
|  |  | BTU | 18000 | 24000 | 30000 | 36000 | 48000 | 60000
|  | Input | W | 1900 | 2720 | 3250 | 3850 | 5540 | 6810
|  | Rated current | A | 8.73 | 12.83 | 15 | 6.9 | 10.1 | 12.43
|  | EER |  | 2.6842 | 2.6471 | 2.6154 | 2.5974 | 2.5271 | 2.4963
Heating |  | Capacity | W | 5600 | 7900 | 9300 | 11000 | 15000 | 17500
|  |  | BTU | 19800 | 26400 | 33000 | 39600 | 52800 | 66000
|  | Input | W | 1750 | 2500 | 3130 | 3680 | 5500 | 6680
|  | Rated current | A | 8.11 | 12 | 14.3 | 6.6 | 10 | 12.13
|  | COP |  | 3.2 | 3.16 | 2.9712 | 2.9891 | 2.7273 | 2.6198
Max. input consumption |  |  | W | 2650 | 3200 | 4100 | 4570 | 6100 | 7800
Max. current |  |  | A | 12.0455 | 14.5455 | 18.6364 | 20.7727 | 27.7273 | 35.4545
Compressor |  | Model |  | SHZ83LC4-E | SHW73TC4-E | PH370X3CJ-3MTS | SHV73YC1-E | C-SBR145H16P | C-SBR165H16P
|  | Type |  | ROTARY | ROTARY | ROTARY | ROTARY | SCROLL | SCROLL
|  | Brand |  | HITACHI | HITACHI | TOSHIBA | HITACHI | SANYO | SANYO
|  | Capacity | W | 6030 | 7330 | 7920 | 8520 | 14200 | 16700
|  | Input | W | 2025 | 2445 | 2610 | 2940 | 4550 | 5300
|  | Rated current(RLA) | A | 9.4 | 12 | 12.65 | 14.5 | 22.6 | 27.1
|  | Locked rotor Amp(LRA) | A | 42 | 65 | / | 75 | / | /
|  | Thermal protector |  | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 150℃ | Inside Eclass 160℃
|  | Capacitor | uF | 50 | 60 | 55 | 60 | 70 | 80
|  | Refrigerant oil | ml | 600 | 600 | 750 | 875 | 1400 | 1400
Indoor unit | Indoor fan motor | Model |  | YSK35-4 | YSK60-4 | YSK75-4 | YSK75-4 | YSK125-4 | YSK125-4
|  | Brand |  | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO
|  | Output Power | W | 35 | 60 | 75 | 75 | 125 | 125
|  | Capacitor | uF | 3 | 3 | 4 | 4 | 5 | 5
|  | Speed (Hi/Mi/Lo) | r/min | 1050/850/750 | 910/780/690 | 1250/1180/980 | 1250/1180/982 | 1370/1180/1080 | 1370/1180/1080
| Indoor coil | a.Number of row |  | 3 | 3 | 3 | 3 | 3 | 3
|  | b.Tube pitch(a)x row pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
|  | c.Fin spacing | mm | 1.4 | 1.6 | 1.5 | 1.5 | 1.5 | 1.5
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
|  | f.Coil length x height x width | mm | 570×266.5×38.1 | 950×266.5×38.1 | 950×266.5×38.1 | 950×266.5×38.1 | 1333×266.5×38.1 | 1333×266.5×38.1
|  | g.Number of U-Tube |  | 19 | 18 | 18 | 18 | 18 | 18
|  | h. Number of circuits |  | 3 | 6 | 6 | 6 | 6 | 6
|  | i.Heat exchanging area | m2 | 7.1681 | 10 | 10.6172 | 10.6172 | 14.8641 | 14.8641
| Indoor air flow (Hi/Mi/Lo) |  | m3/h | 920/736/644 | 1200/960/840 | 1500/1200/1050 | 1500/1200/1050 | 1800/1440/1260 | 1800/1440/1260
| Rated input Power(cooling/heating) |  | W | 85 | 125 | 156 | 156 | 192 | 192
| Rated current (cooling/heating) |  | A | 0.38636 | 0.56818 | 0.70909 | 0.70909 | 0.87273 | 0.87273
| Moisture Removal |  | (L/h) | 1.5 | 2.1 | 2.6 | 3 | 5.1 | 5.5
| Noise level(Hi/Mi/Lo) |  | dB(A) | 43/40/34 | 46/43/37 | 50/47/41 | 50/47/41 | 51/48/42 | 51/48/42
| Extemal static pressure |  | Pa | 0 | 0 | 0 | 0 | 0 | 0
| Unit dimension (W*H*D) |  | mm | 950x673x243 | 1333x673x243 | 1333x673x243 | 1333x673x243 | 1715x673x243 | 1715x673x243
| Packing (W*H*D) |  | mm | 995x740x320 | 1375x740x320 | 1375x740x320 | 1375x740x320 | 1760x740x320 | 1760x740x320
| Net weight |  | Kg | 25 | 33 | 33 | 33 | 41 | 41
| Gross weight |  | Kg | 29 | 38 | 38 | 38 | 47 | 47
Outdoor unit | Outdoor fan motor | Model |  | YDK65-6C-60 | YDK68-6B-60 | YDK68-6B-60 | YDK120-6C-60 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3
|  | Brand |  | AUX | AUX | AUX | AUX | WEITELI | WEITELI
|  | Output Power | W | 65 | 68 | 68 | 120 | 70 | 70
|  | Capacitor | uF | 4 | 4 | 4 | 6 | 3 | 3
|  | Speed | r/min | 870 | 900 | 900 | 800 | 860 | 860
| Outdoor coil | a.Number of row |  | 2 | 2 | 2 | 2 | 2 | 2
|  | b.Tube pitch(a)x row pitch(b) | mm | 22/19.05 | 25.4×22 | 25.4×22 | 25.4×22 | 22/19.05 | 25.4×22
|  | c.Fin spacing | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7.94， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ7.94， Inner grooved | φ9.52， Inner grooved
|  | f.Coil length x height x width | mm | 760×484×38.1 | 733×660.4×44 | 733×660.4×44 | 844×762×44 | 750×1188×38.1 | 750×1219.5×44
|  | g.Number of U-Tube |  | 24 | 26 | 26 | 30 | 54 | 48
|  | h. Number of circuits |  | 4 | 4 | 4 | 4 | 9 | 8
|  | i.Heat exchanging area | m2 | 17.6575 | 23.9982 | 23.9982 | 31.88 | 38.8502 | 45.3033
| Noise level |  | dB(A) | 55 | 60 | 60 | 60 | 62 | 62
| Unit dimension (W*H*D) |  | mm | 800x590x300 | 800x690x300 | 800x690x300 | 900×790×320 | 945x1255x340 | 945x1255x340
| Packing (W*H*D) |  | mm | 930x660x410 | 930x760x410 | 930x760x410 | 1030×850×430 | 1090x1370x430 | 1090x1370x430
| Net weight |  | Kg | 45 | 56 | 60 | 64 | 97 | 105
| Gross weight |  | Kg | 49 | 60 | 64 | 69 | 110 | 119
| Refrigerant type |  |  | R22 | R22 | R22 | R22 | R22 | R22
| Refrigerant charge |  | g | 1360 | 1732 | 2070 | 2630 | 2630 | 3360
| Design pressure |  | MPa | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
Refrigerant pipe |  | Liquid side | mm | 6.35 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
|  | Gas side | mm | 12.7 | 15.88 | 15.88 | 15.88 | 19.05 | 19.05
|  | Max. refrigerant pipe length | m | 25 | 30 | 30 | 30 | 50 | 50
|  | Max. difference in level | m | 10 | 15 | 15 | 15 | 20 | 20
Operation temperature range |  |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient temperature range(Cooling/Heating) |  |  | ℃ | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24
Application area |  |  | m2 | 20~50 | 30~70 | 35~85 | 40~100 | 60~140 | 80~180
Qty’per 20’& 40’&40HQ(only for reference) |  |  | Set | 52/109/130 | 40/85/100 | 40/85/100 | 38/82/92 | 22/48/54 | 22/48/54

## T3 60Hz R22 DU (hidden)
Return |  | Model |  | ALTDu-H18A2/S3 | ALTDu-H24B2/S3 | ALTDu-H30A2/S3 | ALTDu-H36A2/S3 | ALTDu-H48A2/S3 | ALTDu-H60A2/S3
Power supply |  |  | Ph-V-Hz | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ
Cooling |  | Capacity | W | 5100 | 7200 | 8500 | 10000 | 14000 | 17000
|  |  | BTU | 18000 | 24000 | 30000 | 36000 | 48000 | 60000
|  | Input | W | 1900 | 2720 | 3250 | 3850 | 5540 | 6810
|  | Rated current | A | 8.73 | 12.83 | 15 | 6.9 | 10.1 | 12.43
|  | EER |  | 2.6842 | 2.6471 | 2.6154 | 2.5974 | 2.5271 | 2.4963
Heating |  | Capacity | W | 5600 | 7900 | 9300 | 11000 | 15000 | 17500
|  |  | BTU | 19800 | 26400 | 33000 | 39600 | 52800 | 66000
|  | Input | W | 1750 | 2500 | 3130 | 3680 | 5500 | 6680
|  | Rated current | A | 8.11 | 12 | 14.3 | 6.6 | 10 | 12.13
|  | COP |  | 3.2 | 3.16 | 2.9712 | 2.9891 | 2.7273 | 2.6198
Max. input consumption |  |  | W | 2650 | 3200 | 4100 | 4570 | 6100 | 7800
Max. current |  |  | A | 12.0455 | 14.5455 | 18.6364 | 20.7727 | 27.7273 | 35.4545
Compressor |  | Model |  | SHZ83LC4-E | SHW73TC4-E | PH370X3CJ-3MTS | SHV73YC1-E | C-SBR145H16P | C-SBR165H16P
|  | Type |  | ROTARY | ROTARY | ROTARY | ROTARY | SCROLL | SCROLL
|  | Brand |  | HITACHI | HITACHI | TOSHIBA | HITACHI | SANYO | SANYO
|  | Capacity | W | 6030 | 7330 | 7920 | 8520 | 14200 | 16700
|  | Input | W | 2025 | 2445 | 2610 | 2940 | 4550 | 5300
|  | Rated current(RLA) | A | 9.4 | 12 | 12.65 | 14.5 | 22.6 | 27.1
|  | Locked rotor Amp(LRA) | A | 42 | 65 | / | 75 | / | /
|  | Thermal protector |  | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 150℃ | Inside Eclass 160℃
|  | Capacitor | uF | 50 | 60 | 55 | 60 | 70 | 80
|  | Refrigerant oil | ml | 600 | 600 | 750 | 875 | 1400 | 1400
Indoor unit | Indoor fan motor | Model |  | YSK30-4 | YSK50-4 | YSK85-4 | YSK85-4 | YSK110-4 | YSK110-4
|  | Brand |  | HUATE | HUATE | HUATE | HUATE | HUATE | HUATE
|  | Output Power | W | 30 | 50 | 85 | 85 | 110 | 110
|  | Capacitor | uF | 1.5 | 2 | 2.5 | 3 | 4 | 4
|  | Speed (Hi/Mi/Lo) | r/min | 840/750/690 | 930/800/710 | 1100/1030/970 | 1110/1030/980 | 1040/960/880 | 1040/960/880
| Indoor coil | a.Number of row |  | 3 | 3 | 3 | 3 | 3 | 3
|  | b.Tube pitch(a)x row pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
|  | c.Fin spacing | mm | 1.6 | 1.6 | 1.5 | 1.5 | 1.4 | 1.4
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
|  | f.Coil length x height x width | mm | 920×205×38.1 | 1110×205×38.1 | 1110×205×38.1 | 1110×205×38.1 | 1510×205×38.1 | 1510×205×38.1
|  | g.Number of U-Tube |  | 15 | 15 | 15 | 15 | 15 | 15
|  | h. Number of circuits |  | 5 | 5 | 5 | 5 | 7 | 7
|  | i.Heat exchanging area | m2 | 8.0733 | 9.74 | 10.3378 | 10.3378 | 14.9915 | 14.9915
| Indoor air flow (Hi/Mi/Lo) |  | m3/h | 860/688/602 | 1200/960/840 | 1500/1200/1050 | 1500/1200/1050 | 2050/1640/1435 | 2050/1640/1435
| Rated input Power(cooling/heating) |  | W | 85 | 125 | 156 | 156 | 192 | 192
| Rated current (cooling/heating) |  | A | 0.38636 | 0.56818 | 0.70909 | 0.70909 | 0.87273 | 0.87273
| Moisture Removal |  | (L/h) | 1.5 | 2.1 | 2.6 | 3 | 3.6 | 5.1
| Noise level(Hi/Mi/Lo) |  | dB(A) | 42/39/33 | 45/42/36 | 48/45/39 | 48/45/39 | 50/47/41 | 50/47/41
| Extemal static pressure |  | Pa | 12/30 | 12/30 | 12/30 | 12/30 | 12/30 | 12/30
| Unit dimension (W*H*D) |  | mm | 1110×240×528 | 1305×240×528 | 1305×240×528 | 1305×240×528 | 1705×240×528 | 1705×240×528
| Packing (W*H*D) |  | mm | 1210×280×620 | 1375×280×620 | 1375×280×620 | 1375×280×620 | 1760×280×620 | 1760×280×620
| Net weight |  | Kg | 30 | 34.5 | 34.5 | 34.5 | 44 | 44
| Gross weight |  | Kg | 34 | 39.5 | 39.5 | 39.5 | 50 | 50
Outdoor unit | Outdoor fan motor | Model |  | YDK65-6C-60 | YDK68-6B-60 | YDK68-6B-60 | YDK120-6C-60 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3
|  | Brand |  | AUX | AUX | AUX | AUX | WEITELI | WEITELI
|  | Output Power | W | 65 | 68 | 68 | 120 | 70 | 70
|  | Capacitor | uF | 4 | 4 | 4 | 6 | 3 | 3
|  | Speed | r/min | 870 | 900 | 900 | 800 | 860 | 860
| Outdoor coil | a.Number of row |  | 2 | 2 | 2 | 2 | 2 | 2
|  | b.Tube pitch(a)x row pitch(b) | mm | 22/19.05 | 25.4×22 | 25.4×22 | 25.4×22 | 22/19.05 | 25.4×22
|  | c.Fin spacing | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7.94， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ7.94， Inner grooved | φ9.52， Inner grooved
|  | f.Coil length x height x width | mm | 760×484×38.1 | 733×660.4×44 | 733×660.4×44 | 844×762×44 | 750×1188×38.1 | 750×1219.5×44
|  | g.Number of U-Tube |  | 24 | 26 | 26 | 30 | 54 | 48
|  | h. Number of circuits |  | 4 | 4 | 4 | 4 | 9 | 8
|  | i.Heat exchanging area | m2 | 17.6575 | 23.9982 | 23.9982 | 31.88 | 38.8502 | 45.3033
| Noise level |  | dB(A) | 55 | 60 | 60 | 60 | 62 | 62
| Unit dimension (W*H*D) |  | mm | 800x590x300 | 800x690x300 | 800x690x300 | 900×790×320 | 945x1255x340 | 945x1255x340
| Packing (W*H*D) |  | mm | 930x660x410 | 930x760x410 | 930x760x410 | 1030×850×430 | 1090x1370x430 | 1090x1370x430
| Net weight |  | Kg | 45 | 56 | 60 | 64 | 97 | 105
| Gross weight |  | Kg | 49 | 60 | 64 | 69 | 110 | 119
| Refrigerant type |  |  | R22 | R22 | R22 | R22 | R22 | R22
| Refrigerant charge |  | g | 1360 | 1732 | 2070 | 2630 | 2630 | 3360
| Design pressure |  | MPa | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
Refrigerant pipe |  | Liquid side | mm | 6.35 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
|  | Gas side | mm | 12.7 | 15.88 | 15.88 | 15.88 | 19.05 | 19.05
|  | Max. refrigerant pipe length | m | 25 | 30 | 30 | 30 | 50 | 50
|  | Max. difference in level | m | 10 | 15 | 15 | 15 | 20 | 20
Operation temperature range |  |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient temperature range(Cooling/Heating) |  |  | ℃ | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24
Application area |  |  | m2 | 20~50 | 30~70 | 35~85 | 40~100 | 60~140 | 80~180
Qty’per 20’& 40’&40HQ(only for reference) |  |  | Set | 55/120/144 | 47/99/118 | 47/99/118 | 45/90/108 | 25/54/61 | 25/54/61

## T3 60Hz R22 HI (hidden)
Return |  | Model |  | ALTHi-H18A2/S3 | ALTHi-H24B2/S3 | ALTHi-H30A2/S3 | ALTHi-H36A2/S3 | ALTHi-H48A2/S3 | ALTHi-H60A2/S3
Power supply |  |  | Ph-V-Hz | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ | 1Ph / 208-230V/60HZ
Cooling |  | Capacity | W | 5100 | 7200 | 8500 | 10000 | 14000 | 17000
|  |  | BTU | 18000 | 24000 | 30000 | 36000 | 48000 | 60000
|  | Input | W | 1900 | 2720 | 3250 | 3850 | 5540 | 6810
|  | Rated current | A | 8.73 | 12.83 | 15 | 6.9 | 10.1 | 12.43
|  | EER |  | 2.6842 | 2.6471 | 2.6154 | 2.5974 | 2.5271 | 2.4963
Heating |  | Capacity | W | 5600 | 7900 | 9300 | 11000 | 15000 | 17500
|  |  | BTU | 19800 | 26400 | 33000 | 39600 | 52800 | 66000
|  | Input | W | 1750 | 2500 | 3130 | 3680 | 5500 | 6680
|  | Rated current | A | 8.11 | 12 | 14.3 | 6.6 | 10 | 12.13
|  | COP |  | 3.2 | 3.16 | 2.9712 | 2.9891 | 2.7273 | 2.6198
Max. input consumption |  |  | W | 2650 | 3200 | 4100 | 4570 | 6100 | 7800
Max. current |  |  | A | 12.0455 | 14.5455 | 18.6364 | 20.7727 | 27.7273 | 35.4545
Compressor |  | Model |  | SHZ83LC4-E | SHW73TC4-E | PH370X3CJ-3MTS | SHV73YC1-E | C-SBR145H16P | C-SBR165H16P
|  | Type |  | ROTARY | ROTARY | ROTARY | ROTARY | SCROLL | SCROLL
|  | Brand |  | HITACHI | HITACHI | TOSHIBA | HITACHI | SANYO | SANYO
|  | Capacity | W | 6030 | 7330 | 7920 | 8520 | 14200 | 16700
|  | Input | W | 2025 | 2445 | 2610 | 2940 | 4550 | 5300
|  | Rated current(RLA) | A | 9.4 | 12 | 12.65 | 14.5 | 22.6 | 27.1
|  | Locked rotor Amp(LRA) | A | 42 | 65 | / | 75 | / | /
|  | Thermal protector |  | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 125℃ | Inside Eclass 150℃ | Inside Eclass 160℃
|  | Capacitor | uF | 50 | 60 | 55 | 60 | 70 | 80
|  | Refrigerant oil | ml | 600 | 600 | 750 | 875 | 1400 | 1400
Indoor unit | Indoor fan motor | Model |  | YSK100-4 | YSK160-4 | YSK160-4 | YSK180-4 | YSK180-4 | YSK180-4
|  | Brand |  | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO | KANGBAO
|  | Output Power | W | 100 | 160 | 160 | 180 | 180 | 180
|  | Capacitor | uF | 3 | 2.5 | 3 | 5 | 6 | 6
|  | Speed (Hi/Mi/Lo) | r/min | 960/860/840 | 1050/1000/910 | 1100/1000/850 | 1050/1000/910 | 1100/990/920 | 1100/990/920
| Indoor coil | a.Number of row |  | 2 | 3 | 3 | 3 | 3 | 3
|  | b.Tube pitch(a)x row pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
|  | c.Fin spacing | mm | 1.5 | 1.6 | 1.5 | 1.5 | 1.6 | 1.6
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
|  | f.Coil length x height x width | mm | 625×369×25.4 | 625×369×38.1 | 625×369×38.1 | 625×369×38.1 | 985×369×38.1 | 985×369×38.1
|  | g.Number of U-Tube |  | 18 | 27 | 27 | 27 | 27 | 27
|  | h. Number of circuits |  | 3 | 5 | 5 | 5 | 9 | 9
|  | i.Heat exchanging area | m2 | 6.9626 | 9.8407 | 9.8407 | 10.444 | 15.5587 | 15.5587
| Indoor air flow (Hi/Mi/Lo) |  | m3/h | 950/760/665 | 1200/960/840 | 1500/1200/1050 | 1500/1200/1050 | 2000/1600/1400 | 2000/1600/1400
| Rated input Power(cooling/heating) |  | W | 149 | 214 | 240 | 260 | 316 | 316
| Rated current (cooling/heating) |  | A | 0.67727 | 0.97273 | 1.0909 | 1.1818 | 1.4364 | 1.4364
| Moisture Removal |  | (L/h) | 1.5 | 2.1 | 2.6 | 3 | 5.1 | 5.5
| Noise level(Hi/Mi/Lo) |  | dB(A) | 44/41/35 | 47/44/38 | 50/47/41 | 50/47/41 | 53/50/44 | 53/50/44
| Extemal static pressure |  | Pa | 50/80 | 50/80 | 50/80 | 50/80 | 50/80 | 50/80
| Unit dimension (W*H*D) |  | mm | 890×290×785 | 890×290×785 | 890×290×785 | 890×290×785 | 1250×290×785 | 1250×290×785
| Packing (W*H*D) |  | mm | 1100×360×870 | 1100×360×870 | 1100×360×870 | 1100×360×870 | 1460×360×870 | 1460×360×870
| Net weight |  | Kg | 34 | 36 | 36 | 36 | 41 | 41
| Gross weight |  | Kg | 40 | 42 | 42 | 42 | 47 | 47
Outdoor unit | Outdoor fan motor | Model |  | YDK65-6C-60 | YDK68-6B-60 | YDK68-6B-60 | YDK120-6C-60 | YDK70-6A-60D-T3 | YDK70-6A-60D-T3
|  | Brand |  | AUX | AUX | AUX | AUX | WEITELI | WEITELI
|  | Output Power | W | 65 | 68 | 68 | 120 | 70 | 70
|  | Capacitor | uF | 4 | 4 | 4 | 6 | 3 | 3
|  | Speed | r/min | 870 | 900 | 900 | 800 | 860 | 860
| Outdoor coil | a.Number of row |  | 2 | 2 | 2 | 2 | 2 | 2
|  | b.Tube pitch(a)x row pitch(b) | mm | 22/19.05 | 25.4×22 | 25.4×22 | 25.4×22 | 22/19.05 | 25.4×22
|  | c.Fin spacing | mm | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
|  | d.Fin material |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
|  | e.Tube outside dia.and material | mm | φ7.94， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ9.52， Inner grooved | φ7.94， Inner grooved | φ9.52， Inner grooved
|  | f.Coil length x height x width | mm | 760×484×38.1 | 733×660.4×44 | 733×660.4×44 | 844×762×44 | 750×1188×38.1 | 750×1219.5×44
|  | g.Number of U-Tube |  | 24 | 26 | 26 | 30 | 54 | 48
|  | h. Number of circuits |  | 4 | 4 | 4 | 4 | 9 | 8
|  | i.Heat exchanging area | m2 | 17.6575 | 23.9982 | 23.9982 | 31.88 | 38.8502 | 45.3033
| Noise level |  | dB(A) | 55 | 60 | 60 | 60 | 62 | 62
| Unit dimension (W*H*D) |  | mm | 800x590x300 | 800x690x300 | 800x690x300 | 900×790×320 | 945x1255x340 | 945x1255x340
| Packing (W*H*D) |  | mm | 930x660x410 | 930x760x410 | 930x760x410 | 1030×850×430 | 1090x1370x430 | 1090x1370x430
| Net weight |  | Kg | 45 | 56 | 60 | 64 | 97 | 105
| Gross weight |  | Kg | 49 | 60 | 64 | 69 | 110 | 119
| Refrigerant type |  |  | R22 | R22 | R22 | R22 | R22 | R22
| Refrigerant charge |  | g | 1360 | 1732 | 2070 | 2630 | 2630 | 3360
| Design pressure |  | MPa | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
Refrigerant pipe |  | Liquid side | mm | 6.35 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
|  | Gas side | mm | 12.7 | 15.88 | 15.88 | 15.88 | 19.05 | 19.05
|  | Max. refrigerant pipe length | m | 25 | 30 | 30 | 30 | 50 | 50
|  | Max. difference in level | m | 10 | 15 | 15 | 15 | 20 | 20
Operation temperature range |  |  | ℃ | 16~32 | 16~32 | 16~32 | 16~32 | 16~32 | 16~32
Ambient temperature range(Cooling/Heating) |  |  | ℃ | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24 | 16~55/-15~24
Application area |  |  | m2 | 20~50 | 30~70 | 35~85 | 40~100 | 60~140 | 80~180
Qty’per 20’& 40’&40HQ(only for reference) |  |  | Set | 42/88/103 | 39/83/96 | 39/83/96 | 36/72/87 | 21/46/51 | 21/46/51